## Dumbo
Filename | Site No | Site Name | PMR Date | FO Engineer | VSWR | VSWR Remarks | Combiner | Combiner Remarks | Grounding | Grounding Remarks | VSAT(Outdoor) | VSAT(Outdoor) Remarks | GPS Antenna and Cable | GPS Antenna and Cable Remarks | Outdoor FTP/STP Cable and RJ45 Connector | Outdoor FTP/STP Cable and RJ45 Connector Remarks | Feeder Cable | Feeder Cable Remarks | ODU and Cables | ODU and Cable Remarks | Radio ODU | RADIO ODU Remarks | Access Point | Access Point Remarks | Antenna (Panel) | Antenna (Panel) Remarks | Backup of XML/Config | Backup of XML/Config Remarks | Microwave RSL | Microwave RSL Remarks | Equipment Label | Equipment Label Remarks | Equipment Housekeeping | Equipment Housekeeping Remarks | Equipment Grounding | Equipment Grounding Remarks | Indoor Cable | Indoor Cable Remarks | Indoor FTP/STP Cable and RJ45 Connector | Indoor FTP/STP Cable and RJ45 Connector Remarks | Surge Suppressor | Surge Suppresor Remarks | CMM/Router | CMM/Router Remarks | 19in Rack | 19in Rack Remarks | Radio IDU | Radio IDU Remarks | Multiplexer | Multiplexer Remarks | ODF Patch Panel | ODF Patch Panel Remarks | Leased Cable Facility | Leased Cable Facility Remarks | VSAT(Indoor) | VSAT(Indoor) Remarks | Synchronization | Synchronization Remarks | DC Power Plant(Rectifiers) | DC Power Plant(Rectifiers) Remarks | Battery Discharge Test | Battery Discharge Test Remarks | TVSS and Surge Protection | TVSS and Surge Protection Remarks | AC Power Plant | AC Power Plant Remarks | Genset and ATS | Genset and ATS Remarks | Commercial Power Line/Wind and Solar Power | Commercial Power Line/Wind and Solar Power Remarks | Tower | Tower Remarks | Radio Room | Radio Room Remarks | Premise | Premise Remarks | Site Photo | Site Photo Remarks | Reviewed By Supervisor | Site Class | Date | Site Address | Site Category | Radio Room Location | Power Type | Site Type | Tower Type and Height | Shelter Type | Access Hours | Entry Method | NTC License Posting | Valid Until | Lessor's Name | Lessor's Contact No | Longitude | Latitude | Lessor's Address | Perimeter Lights | Gate Status | Perimeter Wall/Fence Status | Padlock Status | Perimeter Area Cleanliness | Perimeter and Premise Remarks | Tower Light | Antenna Condition | MW LOS Checking | Lightning Arrester | Tower Cable Grooming | Tower Grounding | Bus Bar Termination | Shelter Wall/Flooring Condition | Fire Extinguisher | Shelter Cable Tray | Shelter Lighting Fixtures | Shelter Cable Grooming | Shelter Grounding | Shelter Emergency Lights | Shelter Cable Labeling | Port Hole Sealing | Shelter Cleanliness | Shelter Remarks | ACU 1 Type | ACU 2 Type | ACU 3 Type | ACU 1 PN/Model | ACU 2 PN/Model | ACU 3 PN/Model | ACU 1 SN | ACU 2 SN | ACU 3 SN | ACU 1 Status | ACU 2 Status | ACU 3 Status | ACU 1 Ampere Reading | ACU 2 Ampere Reading | ACU 3 Ampere Reading | Exhaust Fan 1 PN/Model | Exhaust Fan 2 PN/Model | Genset | Exhaust Fan 1 Status | Exhaust Fan 2 Status | Genset Brand | ATS | ACU Controller | Genset Rating | MTS | Electric Meter CF Rating | Genset Running Hours | TVSS/Surge Suppressor | Electric Meter No | Day Tank Status | Illegal Tapping | Reserve Diesel (in Liters) | Electric Bill SIN No | Genset Warm Up | No of Empty Drums | Genset Base Pad | Support Facilities Remarks | 2G 1800 Eqpt | 2G 1800 SN/SCF | 2G 900 Eqpt | 2G 900 SN/SCF | 3G 2100 Eqpt | 3G 2100 SN/XML | 3G 850 Eqpt | 3G 850 SN/XML | Wimax No. of CAP | Wimax SN | BRO Router | BRO No. of AP | BRO SN | BTS Alarms Clearing | FD LTE Eqpt | FD LTE SN/XML | TD LTE Eqpt | TD LTE SN/XML | Metro Wifi No. of AP | Metro Wifi SN | BTS Remarks | Eqpt Cleaning | Eqpt Label | MW 1 Brand | MW 1 Model | MW 1 Protected | MW 1 UL Freq | MW 1 DL Freq | MW 1 RSL | MW 1 LOS | MW 1 Card Tag | MW 1 Dual Feed | MW 1 Facing | MW 2 Brand | MW 2 Model | MW 2 Protected | MW 2 UL Freq | MW 2 DL Freq | MW 2 RSL | MW 2 LOS | MW 2 Card Tag | MW 2 Dual Feed | MW 2 Facing | MW 3 Brand | MW 3 Model | MW 3 Protected | MW 3 UL Freq | MW 3 DL Freq | MW 3 RSL | MW 3 LOS | MW 3 Card Tag | MW 3 Dual Feed | MW 3 Facing | MW 4 Brand | MW 4 Model | MW 4 Protected | MW 4 UL Freq | MW 4 DL Freq | MW 4 RSL | MW 4 LOS | MW 4 Card Tag | MW 4 Dual Feed | MW 4 Facing | MW 5 Brand | MW 5 Model | MW 5 Protected | MW 5 UL Freq | MW 5 DL Freq | MW 5 RSL | MW 5 LOS | MW 5 Card Tag | MW 5 Dual Feed | MW 5 Facing | VSAT Brand | VSAT model | VSAT Protected | VSAT UL Freq | VSAT DL Freq | VSAT RSL | VSAT LOS | VSAT EB/NO | VSAT Dual Feed | VSAT Facing | Line Driver 1 NE | Line Driver 1 Carrier | Line Driver 1 Brand | Line Driver 1 PL No./Ckt No | Line Driver 2 NE | Line Driver 2 Carrier | Line Driver 2 Brand | Line Driver 2 PL No./Ckt No | Line Driver 3 NE | Line Driver 3 Carrier | Line Driver 3 Brand | Line Driver 3 PL No./Ckt No | Optical Tx 1 Eqpt Brand | Optical Tx 1 Model | Optical Tx 1 Protected | Optical Tx 1 FOC | Optical Tx 1 Dual Feed | Optical Tx 2 Eqpt Brand | Optical Tx 2 Model | Optical Tx 2 Protected | Optical Tx 2 FOC | Optical Tx 2 Dual Feed | Optical Tx 3 Eqpt Brand | Optical Tx 3 Model | Optical Tx 3 Protected | Optical Tx 3 FOC | Optical Tx 3 Dual Feed | Tx Remarks | E1 Inventory 1 | E1 Inventory 1 Port 1 | E1 Inventory 1 Ckt Assignment 1 | E1 Inventory 1 Port 2 | E1 Inventory 1 Ckt Assignment 2 | E1 Inventory 1 Port 3 | E1 Inventory 1 Ckt Assignment 3 | E1 Inventory 1 Port 4 | E1 Inventory 1 Ckt Assignment 4 | E1 Inventory 1 Port 5 | E1 Inventory 1 Ckt Assignment 5 | E1 Inventory 1 Port 6 | E1 Inventory 1 Ckt Assignment 6 | E1 Inventory 2 | E1 Inventory 2 Port 1 | E1 Inventory 2 Ckt Assignment 1 | E1 Inventory 2 Port 2 | E1 Inventory 2 Ckt Assignment 2 | E1 Inventory 2 Port 3 | E1 Inventory 2 Ckt Assignment 3 | E1 Inventory 2 Port 4 | E1 Inventory 2 Ckt Assignment 4 | E1 Inventory 2 Port 5 | E1 Inventory 2 Ckt Assignment 5 | E1 Inventory 2 Port 6 | E1 Inventory 2 Ckt Assignment 6 | E1 Inventory 3 | E1 Inventory 3 Port 1 | E1 Inventory 3 Ckt Assignment 1 | E1 Inventory 3 Port 2 | E1 Inventory 3 Ckt Assignment 2 | E1 Inventory 3 Port 3 | E1 Inventory 3 Ckt Assignment 3 | E1 Inventory 3 Port 4 | E1 Inventory 3 Ckt Assignment 4 | E1 Inventory 3 Port 5 | E1 Inventory 3 Ckt Assignment 5 | E1 Inventory 3 Port 6 | E1 Inventory 3 Ckt Assignment 6 | FE Inventory 1 | FE Inventory 1 Port 1 | FE Inventory 1 NE Assignment 1 | FE Inventory 1 Port 2 | FE Inventory 1 NE Assignment 2 | FE Inventory 1 Port 3 | FE Inventory 1 NE Assignment 3 | FE Inventory 1 Port 4 | FE Inventory 1 NE Assignment 4 | FE Inventory 1 Port 5 | FE Inventory 1 NE Assignment 5 | FE Inventory 1 Port 6 | FE Inventory 1 NE Assignment 6 | FE Inventory 1 Port 7 | FE Inventory 1 NE Assignment 7 | FE Inventory 1 Port 8 | FE Inventory 1 NE Assignment 8 | FE Inventory 1 Port 9 | FE Inventory 1 NE Assignment 9 | FE Inventory 1 Port 10 | FE Inventory 1 NE Assignment 10 | FE Inventory 2 | FE Inventory 2 Port 1 | FE Inventory 2 NE Assignment 1 | FE Inventory 2 Port 2 | FE Inventory 2 NE Assignment 2 | FE Inventory 2 Port 3 | FE Inventory 2 NE Assignment 3 | FE Inventory 2 Port 4 | FE Inventory 2 NE Assignment 4 | FE Inventory 2 Port 5 | FE Inventory 2 NE Assignment 5 | FE Inventory 2 Port 6 | FE Inventory 2 NE Assignment 6 | FE Inventory 2 Port 7 | FE Inventory 2 NE Assignment 7 | FE Inventory 2 Port 8 | FE Inventory 2 NE Assignment 8 | FE Inventory 2 Port 9 | FE Inventory 2 NE Assignment 9 | FE Inventory 2 Port 10 | FE Inventory 2 NE Assignment 10 | ODF Inventory Port 1 | ODF Inventory Core Assignment 1 | ODF Inventory Core Distance Port 1 | ODF Inventory Port 2 | ODF Inventory Core Assignment 2 | ODF Inventory Core Distance Port 2 | ODF Inventory Port 3 | ODF Inventory Core Assignment 3 | ODF Inventory Core Distance Port 3 | ODF Inventory Port 4 | ODF Inventory Core Assignment 4 | ODF Inventory Core Distance Port 4 | ODF Inventory Port 5 | ODF Inventory Core Assignment 5 | ODF Inventory Core Distance Port 5 | ODF Inventory Port 6 | ODF Inventory Core Assignment 6 | ODF Inventory Core Distance Port 6 | ODF Inventory Port 7 | ODF Inventory Core Assignment 7 | ODF Inventory Core Distance Port 7 | ODF Inventory Port 8 | ODF Inventory Core Assignment 8 | ODF Inventory Core Distance Port 8 | ODF Inventory Port 9 | ODF Inventory Core Assignment 9 | ODF Inventory Core Distance Port 9 | ODF Inventory Port 10 | ODF Inventory Core Assignment 10 | ODF Inventory Core Distance Port 10 | Tx Overall Remarks | Rectifier 1 Brand | Rectifier 1 Voltage | Rectifier 1 Battery Current | Rectifier 1 Distribution Current | Rectifier 1 Rectifier Current | Rectifier 1 No. of RM | Rectifier 1 No. of Battery Bank | Rectifier 1 Battery Brand Bank 1 | Rectifier 1 Battery Bank 1 AH | Rectifier 1 Battery Brand Bank 2 | Rectifier 1 Battery Bank 2 AH | Rectifier 1 Battery Brand Bank 3 | Rectifier 1 Battery Bank 3 AH | Rectifier 1 Battery Brand Bank 4 | Rectifier 1 Battery Bank 4 AH | Rectifier 1 Battery Deformities | Rectifier 1 Battery Deformities Bank No | Rectifier 1 Battery Voltage Bank 1 | Rectifier 1 Battery Voltage Bank 2 | Rectifier 1 Battery Voltage Bank 3 | Rectifier 1 Battery Voltage Bank 4 | Rectifier 1 External Alarm Simulation | Rectifier 1 Breaker 1 Ampere Rating | Rectifier 1 Breaker 1 Load | Rectifier 1 Breaker 2 Ampere Rating | Rectifier 1 Breaker 2 Load | Rectifier 1 Breaker 3 Ampere Rating | Rectifier 1 Breaker 3 Load | Rectifier 1 Breaker 4 Ampere Rating | Rectifier 1 Breaker 4 Load | Rectifier 1 Breaker 5 Ampere Rating | Rectifier 1 Breaker 5 Load | Rectifier 1 Breaker 6 Ampere Rating | Rectifier 1 Breaker 6 Load | Rectifier 1 Breaker 7 Ampere Rating | Rectifier 1 Breaker 7 Load | Rectifier 1 Breaker 8 Ampere Rating | Rectifier 1 Breaker 8 Load | Rectifier 1 Breaker 9 Ampere Rating | Rectifier 1 Breaker 9 Load | Rectifier 1 Breaker 10 Ampere Rating | Rectifier 1 Breaker 10 Load | Rectifier 1 Breaker 11 Ampere Rating | Rectifier 1 Breaker 11 Load | Rectifier 1 Breaker 12 Ampere Rating | Rectifier 1 Breaker 12 Load | Rectifier 1 Breaker 13 Ampere Rating | Rectifier 1 Breaker 13 Load | Rectifier 1 Breaker 14 Ampere Rating | Rectifier 1 Breaker 14 Load | Rectifier 1 Breaker 15 Ampere Rating | Rectifier 1 Breaker 15 Load | Rectifier 1 Breaker 16 Ampere Rating | Rectifier 1 Breaker 16 Load | Rectifier 1 Breaker 17 Ampere Rating | Rectifier 1 Breaker 17 Load | Rectifier 1 Breaker 18 Ampere Rating | Rectifier 1 Breaker 18 Load | Rectifier 1 Breaker 19 Ampere Rating | Rectifier 1 Breaker 19 Load | Rectifier 1 Breaker 20 Ampere Rating | Rectifier 1 Breaker 20 Load | Rectifier 1 Breaker 21 Ampere Rating | Rectifier 1 Breaker 21 Load | Rectifier 1 Breaker 22 Ampere Rating | Rectifier 1 Breaker 22 Load | Rectifier 2 Brand | Rectifier 2 Voltage | Rectifier 2 Battery Current | Rectifier 2 Distribution Current | Rectifier 2 Rectifier Current | Rectifier 2 No. of RM | Rectifier 2 No. of Battery Bank | Rectifier 2 Battery Brand Bank 1 | Rectifier 2 Battery Bank 1 AH | Rectifier 2 Battery Brand Bank 2 | Rectifier 2 Battery Bank 2 AH | Rectifier 2 Battery Brand Bank 3 | Rectifier 2 Battery Bank 3 AH | Rectifier 2 Battery Brand Bank 4 | Rectifier 2 Battery Bank 4 AH | Rectifier 2 Battery Deformities | Rectifier 2 Battery Deformities Bank No | Rectifier 2 Battery Voltage Bank 1 | Rectifier 2 Battery Voltage Bank 2 | Rectifier 2 Battery Voltage Bank 3 | Rectifier 2 Battery Voltage Bank 4 | Rectifier 2 External Alarm Simulation | Rectifier 2 Breaker 1 Ampere Rating | Rectifier 2 Breaker 1 Load | Rectifier 2 Breaker 2 Ampere Rating | Rectifier 2 Breaker 2 Load | Rectifier 2 Breaker 3 Ampere Rating | Rectifier 2 Breaker 3 Load | Rectifier 2 Breaker 4 Ampere Rating | Rectifier 2 Breaker 4 Load | Rectifier 2 Breaker 5 Ampere Rating | Rectifier 2 Breaker 5 Load | Rectifier 2 Breaker 6 Ampere Rating | Rectifier 2 Breaker 6 Load | Rectifier 2 Breaker 7 Ampere Rating | Rectifier 2 Breaker 7 Load | Rectifier 2 Breaker 8 Ampere Rating | Rectifier 2 Breaker 8 Load | Rectifier 2 Breaker 9 Ampere Rating | Rectifier 2 Breaker 9 Load | Rectifier 2 Breaker 10 Ampere Rating | Rectifier 2 Breaker 10 Load | Rectifier 2 Breaker 11 Ampere Rating | Rectifier 2 Breaker 11 Load | Rectifier 2 Breaker 12 Ampere Rating | Rectifier 2 Breaker 12 Load | Rectifier 2 Breaker 13 Ampere Rating | Rectifier 2 Breaker 13 Load | Rectifier 2 Breaker 14 Ampere Rating | Rectifier 2 Breaker 14 Load | Rectifier 2 Breaker 15 Ampere Rating | Rectifier 2 Breaker 15 Load | Rectifier 2 Breaker 16 Ampere Rating | Rectifier 2 Breaker 16 Load | Rectifier 2 Breaker 17 Ampere Rating | Rectifier 2 Breaker 17 Load | Rectifier 2 Breaker 18 Ampere Rating | Rectifier 2 Breaker 18 Load | Rectifier 2 Breaker 19 Ampere Rating | Rectifier 2 Breaker 19 Load | Rectifier 2 Breaker 20 Ampere Rating | Rectifier 2 Breaker 20 Load | Rectifier 2 Breaker 21 Ampere Rating | Rectifier 2 Breaker 21 Load | Rectifier 2 Breaker 22 Ampere Rating | Rectifier 2 Breaker 22 Load | Rectifier 3 Brand | Rectifier 3 Voltage | Rectifier 3 Battery Current | Rectifier 3 Distribution Current | Rectifier 3 Rectifier Current | Rectifier 3 No. of RM | Rectifier 3 No. of Battery Bank | Rectifier 3 Battery Brand Bank 1 | Rectifier 3 Battery Bank 1 AH | Rectifier 3 Battery Brand Bank 2 | Rectifier 3 Battery Bank 2 AH | Rectifier 3 Battery Brand Bank 3 | Rectifier 3 Battery Bank 3 AH | Rectifier 3 Battery Brand Bank 4 | Rectifier 3 Battery Bank 4 AH | Rectifier 3 Battery Deformities | Rectifier 3 Battery Deformities Bank No | Rectifier 3 Battery Voltage Bank 1 | Rectifier 3 Battery Voltage Bank 2 | Rectifier 3 Battery Voltage Bank 3 | Rectifier 3 Battery Voltage Bank 4 | Rectifier 3 External Alarm Simulation | Rectifier 3 Breaker 1 Ampere Rating | Rectifier 3 Breaker 1 Load | Rectifier 3 Breaker 2 Ampere Rating | Rectifier 3 Breaker 2 Load | Rectifier 3 Breaker 3 Ampere Rating | Rectifier 3 Breaker 3 Load | Rectifier 3 Breaker 4 Ampere Rating | Rectifier 3 Breaker 4 Load | Rectifier 3 Breaker 5 Ampere Rating | Rectifier 3 Breaker 5 Load | Rectifier 3 Breaker 6 Ampere Rating | Rectifier 3 Breaker 6 Load | Rectifier 3 Breaker 7 Ampere Rating | Rectifier 3 Breaker 7 Load | Rectifier 3 Breaker 8 Ampere Rating | Rectifier 3 Breaker 8 Load | Rectifier 3 Breaker 9 Ampere Rating | Rectifier 3 Breaker 9 Load | Rectifier 3 Breaker 10 Ampere Rating | Rectifier 3 Breaker 10 Load | Rectifier 3 Breaker 11 Ampere Rating | Rectifier 3 Breaker 11 Load | Rectifier 3 Breaker 12 Ampere Rating | Rectifier 3 Breaker 12 Load | Rectifier 3 Breaker 13 Ampere Rating | Rectifier 3 Breaker 13 Load | Rectifier 3 Breaker 14 Ampere Rating | Rectifier 3 Breaker 14 Load | Rectifier 3 Breaker 15 Ampere Rating | Rectifier 3 Breaker 15 Load | Rectifier 3 Breaker 16 Ampere Rating | Rectifier 3 Breaker 16 Load | Rectifier 3 Breaker 17 Ampere Rating | Rectifier 3 Breaker 17 Load | Rectifier 3 Breaker 18 Ampere Rating | Rectifier 3 Breaker 18 Load | Rectifier 3 Breaker 19 Ampere Rating | Rectifier 3 Breaker 19 Load | Rectifier 3 Breaker 20 Ampere Rating | Rectifier 3 Breaker 20 Load | Rectifier 3 Breaker 21 Ampere Rating | Rectifier 3 Breaker 21 Load | Rectifier 3 Breaker 22 Ampere Rating | Rectifier 3 Breaker 22 Load | Main AC Breaker Rating | Main AC Load | AC Breaker 1 Rating | AC Breaker 1 Load | AC Breaker 2 Rating | AC Breaker 2 Load | AC Breaker 3 Rating | AC Breaker 3 Load | AC Breaker 4 Rating | AC Breaker 4 Load | AC Breaker 5 Rating | AC Breaker 5 Load | AC Breaker 6 Rating | AC Breaker 6 Load | AC Breaker 7 Rating | AC Breaker 7 Load | AC Breaker 8 Rating | AC Breaker 8 Load | AC Breaker 9 Rating | AC Breaker 9 Load | AC Breaker 10 Rating | AC Breaker 10 Load | AC Breaker 11 Rating | AC Breaker 11 Load | AC Breaker 12 Rating | AC Breaker 12 Load | AC Breaker 13 Rating | AC Breaker 13 Load | AC Breaker 14 Rating | AC Breaker 14 Load | AC Breaker 15 Rating | AC Breaker 15 Load | AC Breaker 16 Rating | AC Breaker 16 Load | AC Breaker 17 Rating | AC Breaker 17 Load | AC Breaker 18 Rating | AC Breaker 18 Load | AC Breaker 19 Rating | AC Breaker 19 Load | AC Breaker 20 Rating | AC Breaker 20 Load | Site Pictures | Site Log Book | Other Issues and Concerns | Supervisor | Date Signed | ARDS Item 1 | ARDS Quantity 1 | ARDS Details 1 | ARDS c/o 1 | ARDS Item 2 | ARDS Quantity 2 | ARDS Details 2 | ARDS c/o 2 | ARDS Item 3 | ARDS Quantity 3 | ARDS Details 3 | ARDS c/o 3 | ARDS Item 4 | ARDS Quantity 4 | ARDS Details 4 | ARDS c/o 4 | ARDS Item 5 | ARDS Quantity 5 | ARDS Details 5 | ARDS c/o 5 | ARDS Item 6 | ARDS Quantity 6 | ARDS Details 6 | ARDS c/o 6 | ARDS Item 7 | ARDS Quantity 7 | ARDS Details 7 | ARDS c/o 7 | ARDS Item 8 | ARDS Quantity 8 | ARDS Details 8 | ARDS c/o 8 | ARDS Item 9 | ARDS Quantity 9 | ARDS Details 9 | ARDS c/o 9 | ARDS Item 10 | ARDS Quantity 10 | ARDS Details 10 | ARDS c/o 10 | Deficiency Item 1 | Deficiency Description 1 | Deficiency Item No. 1 | Deficiency Item Brand 1 | Deficiency Item Model 1 | Deficiency Item Rating 1 | Deficiency Item Serial No. 1 | Deficeincy Item 2 | Deficiency Description 2 | Deficiency Item No. 2 | Deficiency Item Brand 2 | Deficiency Item Model 2 | Deficiency Item Rating 2 | Deficiency Item Serial No. 2 | Deficiency Item 3 | Deficiency Description 3 | Deficiency Item No. 3 | Deficiency Item Brand 3 | Deficiency Item Model 3 | Deficiency Item Rating 3 | Deficiency Item Serial No. 3 | Deficiency Item 4 | Deficiency Description 4 | Deficiency Item No. 4 | Deficiency Item Brand 4 | Deficiency Item Model 4 | Deficiency Item Rating 4 | Deficiency Item Serial No. 4 | Deficiency Item 5 | Deficiency Description 5 | Deficiency Item No. 5 | Deficiency Item Brand 5 | Deficiency Item Model 5 | Deficiency Item Rating 5 | Deficiency Item Serial No. 5 | Deficiency Item 6 | Deficiency Description 6 | Deficiency Item No. 6 | Deficiency Item Brand 6 | Deficiency Item Model 6 | Deficiency Item Rating 6 | Deficiency Item Serial No. 6 | Deficiency Item 7 | Deficiency Description 7 | Deficiency Item No. 7 | Deficiency Item Brand 7 | Deficiency Item Model 7 | Deficiency Item Rating 7 | Deficiency Item Serial No. 7 | Deficiency Item 8 | Deficiency Description 8 | Deficiency Item No. 8 | Deficiency Item Brand 8 | Deficiency Item Model 8 | Deficiency Item Rating 8 | Deficiency Item Serial No. 8 | Deficiency Item 9 | Deficiency Description 9 | Deficiency Item No. 9 | Deficiency Item Brand 9 | Deficiency Item Model 9 | Deficiency Item Rating 9 | Deficiency Item Serial No. 9 | Deficiency Item 10 | Deficiency Description 10 | Deficiency Item No. 10 | Deficiency Item Brand 10 | Deficiency Item Model 10 | Deficiency Item Rating 10 | Deficiency Item Serial No. 10 | Deficiency Item 11 | Deficiency Description 11 | Deficiency Item No. 11 | Deficiency Item Brand 11 | Deficiency Item Model 11 | Deficiency Item Rating 11 | Deficiency Item Serial No. 11 | Deficiency Item 12 | Deficiency Description 12 | Deficiency Item No. 12 | Deficiency Item Brand 12 | Deficiency Item Model 12 | Deficiency Item Rating 12 | Deficiency Item Serial No. 12 | Site Premise Remarks | Site Tower Remarks | Site Equipment(1) Remarks | Site Equipment(2) Remarks | Site BTS Equipment Remarks | Site Transmission Equipment Remarks | Site Genset and Day Tank Remarks | Site Deficiency Remarks
3306 Buenavista.pdf | 3306 | Buenavista | 2017-03-24 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | CEILING AND VAN FOR REHAB | Rectification | PERIMETER FENCE FOR REPAIR | OK |  |  | Off |  | Brgy Poblacion, Buenavista, Bohol | RESIDENTIAL | LOT | PERMANENT | LOT | SST 150FT | ROOM | 24HRS | CARETAKER | Yes |  | Ricardo Mero SR. | 09772878749/09287679577 | 124.107074° | 10.084908° | Brgy Poblacion, Buenavista, Bohol | 3,1 | OK | for CSMP Endo | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 6,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | FP-51QSXRACCONR19KEDP1C | WCONA019ED |  | 51QSXRACCONR19KEDN10PC-0470082 | 51QSXRACCONR19KEDA11PC-0083342 |  | Working | Working | None | 8 | 9 |  |  |  | 1,0 | Defective | Defective | DENYO | Working | None | 25 | Working | Off | 310.5 | None | 18249273 | Working | None | 11.5 inches |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900+RRU | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | No | 7747.7 | 8059.02 | -34.6 | OK | OK | Yes | JETAFE | HUAWEI | RTN950 | No | 7429 | 7233 | -35.1 | OK | OK | Yes | INABANGA | HUAWEI | RTN950 | Yes | 7121 | 7317 | 5.046 | OK | OK | Yes | INABANGA LAPACAN SUR |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | RTN INABANGA | 1 | BUENAVISTA 2G 1ST E1 | 2 | BUENAVISTA 2G 2ND E1 | 3 | INABANGA LAPACAN SUR 2G | 4 | JETAFE 2G 1ST E1 | 5 | JETAFE 2G 2ND E1 |  |  | RTN JETAFE | 1 | JETAFE 2G 1ST E1 | 2 | JETAFE 2G 2ND E1 | [8 empty] | RTN INABANGA LAPACAN SUR | 1 | INABANGA LAPACAN SUR 2G | [10 empty] | RTN JETAFE | 2 | JETAFE 3G | [18 empty] | RTN INABANGA | 1 | JETAFE 3G | 2 | BUENAVISTA 3G | [47 empty] | ELTEK | 54.01 | 0 | 47 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 51.8 | 51.6 | 51.4 |  | OK | 100 | BTS3900L LOWER | 100 | BTS3900L UPPER | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G DCDU | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 | RTN INABANGA A | 16 | MINILINK JETAFE | 16 | RTN INABANGA LAPACAN A | 16 | NFH INABANGA | 16 | RTN JETAFE A | EMERSON | 52.2 |  | 0 |  | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No |  | 53 | 53 |  |  | Off | 6 | BATTERY | 6 |  | 16 | RTN INABANGA LAPACAN B | 16 | RTN INABANGA B | 40 |  | 40 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | RTN JETAFE B | [33 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 30 | 70 | EMERSON | 70 | ELTEK1 | 40 | ACU 2 | 40 | ELTEK 2 | 20 | VAN LIGHTS | 20 | C.O. | 20 | P AND T LIGHTS | 40 | ACU 1 | [24 empty] | Done | OK | [43 empty] | CIVIL | EQUIPMENT SHELTER | [5 empty] | CIVIL | PERIMETER FENCE | [5 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING
3311 Catigbian.pdf | 3311 | Catigbian | 2017-03-09 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | Off |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | GENSET BATTERY FOR REPLACEMENT; DEFECTIVE ATS | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy Poblacion, West E, Catigbian, Bohol | RESIDENTIAL | LOT | PERMANENT | LOT | SST 150FT. | VAN | 24HRS | CARETAKER | Yes |  | Samuel Baloma |  | 124° 0'9.03"E | 9°51'13.87"N | Brgy Poblacion, West E, Catigbian, Bohol | 0,4 | OK | OK | for Replacement | For CSMP Endo |  | Defective | Off | Off | OK | Off | Off | OK | OK | OK | OK | 3,1 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | WCONX019ED1 |  | 51PMXRACCAR19KEDT09PC-0529954 | 51QSXRACCON19KEDK13PC-0356982 |  | Working | Working | None | 6.9 | 0.89 |  |  |  | 1,0 | Defective | Defective | DENYO | Defective | Off | 25 | Working | Off | 71.4 | None | 10651956 | Working | Off | 10.5 INCHES |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | No | 8073.85 | 7762.53 | -35.2 | OK | OK | Yes | LOON RS | HUAWEI | RTN950 | No | 7895.95 | 8207.27 | -37.4 | OK | OK | Yes | SAGBAYAN | HUAWEI | RTN950 | No | 7121 | 7317 | -36.5 | Off | Off | Yes | SAN ISIDRO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | FACING LOON RS | 1 | Catigbian 2G 1st E1 | 2 | Catigbian 2G 2nd E1 | 3 | Sagbayan 2G 1st E1 | 4 | Sagbayan 2G 2nd E1 | 5 | San Isidro 2G 1st E1 |  |  | FACING SAGBAYAN | 1 | Sagbayan 2G 1st E1 | 2 | Sagbayan 2G 2nd E1 | [8 empty] | FACING SAN ISIDRO | 1 | San Isidro 2G 1st E1 | [10 empty] | FACING LOON RS | 1 | CATIGBIAN 3G | 2 | SAGBAYAN 3G | 3 | SAN ISIDRO 3G | [14 empty] | FACING SAGBAYAN | 1 | SAGBAYAN 3G | [49 empty] | ELTEK | 54.09 |  | 39 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 52.9 | 52.7 | 52.6 | 52.4 | OK | 80 | BTS3900L UPPER | 16 | RTN 950 SAN ISIDRO A | 80 | BTS3900L LOWER | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G DCDU | 40 | RTN 950 LOON RS A | 40 | RTN 950 LOON RS B | 40 |  | 40 |  | 40 |  | 20 | RTN 950 SAN ISIDRO B | 20 |  | 20 |  | 16 | RTN 950 SAGBAYAN B | 16 | RTN 950 SAGBAYAN A | 16 | NOKIA FH SAN ISIDRO | 100 | [16 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 17.7 | 70 | ELTEK 1 | 70 | ELTEK 2 | 50 |  | 50 |  | 40 |  | 40 |  | 40 |  | 40 |  | 30 | ACU 1 | 30 | PERIMETER LIGHTS | 30 | ACU 2 | 30 | C.O. | 20 | VAN LIGHTS | 20 | TOWER LIGHT | [12 empty] | Done | OK |  |  |  | BATTERIES | 12 | NARADA 12V 100AH | FO & WFM | [36 empty] | ELECTROMECHANICAL | GENSET BATTERY | [5 empty] | ELECTROMECHANIC | PERIMETER LIGHTING | [5 empty] | ELECTROMECHANIC | TOWER LIGHTING
3312 Dagohoy (Camangay RS)_3_10_17.pdf | 3312 | DAGOHOY (CAMANGAYS RS) | 2017-03-10 | FHG/RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | No 3G is installed. | OK | See back page for RSL. | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Dagohoy Bohol | Residential | Lot | Permanent | Lot | 3L-SST and 150 Ft. | Collapsible | 24 Hrs. | Posting Guard | Yes |  | DENR |  | 124° 15’ 8.9” | 09° 54’ 5.1” |  | 42767 | OK | For FASG Endo | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36861 | OK | Ok | None | OK | OK | OK |  | WACU | WACU | Off | FP-51QSXRACCONR19KEDP1C | WCONX019ED1 | FP-51QSXRACCONR19KEDP1C | 51QSXRACCON19KEDR10PC-0505672 | 51QSXRACCON19KEDT15PC-0722338 | 51QSXRACCON19KEDT09PC-0529267 | Working | Working | Off | 7.6A | 6.9A | 6.6A | No brand | No brand | 36557 | Working | Working | Powercity, Denyo | Working | Off | 45, 25 | Working | Off | 1176.0, 9782.6 | Working | 110101005089 | Working | None | 9.5 inches | 17-1791-0003 | Working | N/A | Working | WACU #4: Model#:FP-51QSXRACCONR19KEDP1C, SN#:51QSXRACCON19KEDT09PC-0529358 | BTS 3900L | Retrieved | BTS 3900L | Retrieved |  | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No |  |  |  | Off | Off | Yes | 4325-Danao | Huawei | RTN 950 | No |  |  |  | Off | Off | No | 3305-Pilar | Huawei | RTN 950 | No |  |  |  | Off | Off | Off | V3424-SUN Dagohoy | Nokia | Flexihopper | No | 7359 | 7198 |  | Off | Off | Off | F22-Alicia |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | See attached PDF for other links' RSL & Frequencies | facing Danao | 1 |  | 2 |  | 3 | See attached PDF for E1 inventories | 4 | [5 empty] | facing Pilar | 1 |  | 2 |  | 3 |  | 4 | [5 empty] | facing SUN Dagohoy | [12 empty] | facing Danao | 1 |  | 2 | See attached PDF for FE inventories | 3 |  | 4 | [13 empty] | facing Pilar | [50 empty] | See attached PDF for E1 and FE inventories | Eltek #1 | 54.23V | 0.0A | 4.0A | 4.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 52.4V | 52.4V | 52.4V | 52.4V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 | DFB B | 63 |  | 63 |  | 63 |  | 63 |  | 40 | FUJITSU DEHYDRATOR | 40 | FUJITSU BLOCK B | 40 |  | 40 |  | 40 | RTN facing Loon RS Rdnt | 40 | XDM-100 A | 20 | RTN facing Alicia Rdnt | 20 | RTN facing Pilar Rdnt | 20 | RTN facing Danao Rdnt | 16 | Aviat DCPDB A | 16 | RTN facing SUN Dagohoy Rdnt | 80 | Hopper facing Danao | 80 | DC Fan | Eltek #2 | 54.72V | 0.0A | 26.0A | 26.0A | 4 | 4 | Lynx | 170 | Lynx | 170 | Lynx | 170 | Lynx | 170 | No |  | 50.6V | 50.6v | 50.5V | 50.4V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 |  | 80 |  | 80 |  | 63 | DFB A | 63 |  | 63 |  | 63 |  | 40 | XDM-100 B | 40 | RTN facing Loon RS Main | 40 |  | 40 | RTN facing Alicia Main | 20 | RTN facing Pilar Main | 20 | RTN facing Danao Main | 20 | RTN facing SUN Dagohoy Main | 20 | Hopper facing Pilar | 10 | Hopper facing Alicia | 10 | Aviat DCPDB B | ZTE (Left) | 53.8V | 0.0A | 37.3A | 37.3A | 3 | 2 | Sacred Sun | 180 | Sacred Sun | 180 |  |  |  |  | No |  | 50.0V | 50.0V |  |  | OK | 100 |  | 100 |  | 63 | DMR 5000S (A1) | 63 |  | 63 |  | 63 |  | 50 |  | 50 | BTS 3900L UPPER | 80 |  | 40 | BTS 3900L LOWER | 40 | OSN 2500NE135 POWER A | 40 |  | 40 | [19 empty] | 100 | 34.3 | 70 | Eltek 2A | 70 | Eltek 1B | 50 | Eltek 1A | 50 | Eltek 2B | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | SPARE | 30 | ACU 1 | 30 | SPARE | 30 | ACU 2 | 20 | LIGHTINGS | 20 | OUTLET | [12 empty] | Done | OK |  |  |  | WACU | 1 unit | Condura 2HP / SN: 048406951 | WFM, FO | WACU | 1 unit | Condura 2HP / SN: 048408035 | WFM, FO | Rectifier | 1 unit | Empower / SN: 2472605 | WFM, FO | Rectifier | 1 unit | Emerson / SN: X481084530 | WFM, FO | [24 empty] | Civil | Perimeter Fence | 1 Lot | [88 empty] | Perimeter barb wire for rehab.
3314 Cortes_1_12_17.pdf | 3314 | CORTES | 2017-01-12 | FHG/MRR/RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | 3G xml | OK | -36.4 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed. | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek: 54.8V, 54.8V, 54.8V Powerone: 54.3V, 54.3V | OK | Passed. | N/A |  | OK |  | OK | Genset has defective start/stop solenoid. Already had Work Order to CSMP. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Cortes, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower, 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Manuel Calibo | 9338620055 | 123° 52’ 50” | 09° 43’ 23” | Brgy. Poblacion, Cortes, Bohol | 2017-02-02 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-03-01 | OK | Ok | 0/0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDK15PC-0540061 | 51QSXRACCON19KEDF09PC-0275998 |  | Working | Working | Off | 7.1A | 7.0A |  |  |  | 2000-01-01 | None | None | Shinsetsu | Working | None | 25 | Working | Off | 537.2 | None | 14655929 | None | None | 320 | 1818011145 | Working | 1 | None | Ongoing construction of genset pad and fuel tank pedestal. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 7358.5 | 7197.5 | -36.4 | OK | OK | Yes | V3384-SUN Antequera |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 | Cortes 2G 1st E1 | 2 | Cortes 2G 2nd E1 | 3 | SUN Antequera 2G 1st E1 | 4 | SUN Antequera 2G 2nd E1 |  |  |  |  | SUN Antequera | 1 | SUN Antequera 2G 1st E1 | 2 | SUN Antequera 2G 2nd E1 | 3 |  | 4 | [18 empty] | Huawei CEN | 1 | Cortes 3G-2100 | 2 |  | 3 | BISU-Balilihan Leased Line | 4 |  | 5 |  | 6 |  | 7 |  | 8 | [5 empty] | SUN Antequera | 1 | SUN Antequera 2G-1800 1st E1 | 2 | SUN Antequera 2G-1800 2nd E1 | 3 |  | 4 |  | 5 |  | 6 | [40 empty] | Eltek | 54.58V | 0.0A | 20.0A | 20.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 54.8V | 54.8V | 54.8V |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G-2100 DCDU | 40 |  | 40 |  | 40 |  | 40 |  | 40 | NE40E-X2-M8 RDNT | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 | RTN facing SUN Antequera Main | 16 | MLTN facing SUN Antequera | Powerone | 54.16V | 0.0A | 23.2A | 23.2A | 2 | 2 | Powersafe | 170 | Powersafe | 170 |  |  |  |  | No |  | 54.3V | 54.3V |  |  | OK | 50 |  | 50 |  | 63 |  | 63 |  | 40 | NE40E-X2-M8 MAIN | 6 |  | 16 |  | 16 |  | 16 | RTN facing SUN Antequera Rdnt | 10 |  | 10 |  | 10 |  | 10 |  |  |  | 80 | BTS 3900L LOWER |  |  | 80 | BTS 3900L UPPER | [25 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25.2 | 70 | ELTEK 1 | 70 | POWERONE | 50 | SPARE | 50 | ELTEK 2 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | ACU 2 | 30 | TOWER LIGHT | 30 | ACU 1 | 30 | PERIMETER LIGHTS | 20 | VAN LIGHTS | 20 | VAN LIGHTS | [12 empty] | Done | OK |  |  |  | Standby Genset | 1 | Denyo 25KVA / S.N. 5429297 | WFM, FO | [36 empty] | Civil | Others (Shelter Roofing)) | [89 empty] | For roof rehab.
3336 Laka RS_2_6_17.pdf | 3336 | LAKA RS | 2017-02-06 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A | Only 2G service is installed. | OK | See attached PDF for RSL | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | OK | Router is installed on site while the CMM is @V5317 Anda Candabong. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | Emerson: 53.6V, 53.6V Eltek: 53.6V, 53.6V, 53.6V | OK | Passed. | OK |  | OK |  | OK |  | OK |  | Rectification | Ongoing rectification of corroded tower parts by Falco. | OK |  | OK |  | OK |  |  | Off |  | Brgy. Laca. Jagna, Bohol | Residential | Lot | Permanent | Lot | 4L-SST / 180 Ft. | Collapsible | 24 Hrs. | Posting Guard | Yes |  | Virgilio Virtudazo | 9165294996 | 124° 20’ 7.1” | 09° 39’ 23” | Brgy. De Lapaz, Cortes, Bohol | 2000-04-01 | OK | for CSMP Endo | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-06-02 | OK | Ok | 0/1 | OK | OK | OK |  | Off | Off | Off | FP-51QSXRACCONR19KEDP1C | FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDH10PC-0380045 | 51QSXRACCON19KEDH10PC-0380064 |  | Working | Working | Off | 7.5 A | 7.6 A |  | No brand/Model | No brand/Model | 2000-02-01 | Working | Working | Denyo, Powercity | Working | None | 25, 60 | Working | CF100 | 1670.7, 0302.7 | Working | 100501016948 | Working | Off | 500 | 03-0391-0080 | Working | N/A | Working |  |  | Off | BTS 3900L | Retrieved |  | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Nokia | Flexihopper | No | 7352 | 7191 | -33 | OK | OK | No | 4326-Duero |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | See attached PDF for other links' RSL & Frequencies | Duero | 1 | Duero 2G-900 1st E1 | 2 | Duero 3G-2100 1st E1 | 3 | Duero 3G-2100 1st E1 | [12 empty] | Please see attachment for other links' E1 inventory | [48 empty] | Please see attachment for other links' FE |  | inventory | [41 empty] | Eltek | 54.05V | 0.0A | 27.0A | 27.0A | 4 | 3 | Narada | 155 | Narada | 155 | Narada | 155 |  |  | No |  | 53.6V | 53.6V | 53.6V |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 | BTS 3900L Upper | 80 | BTS 3900L Lower | 80 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 | RTN facing Anda Main | 40 | Harris facing Gorda RS B | 40 | Harris DCPDB B | 20 |  | 20 | Bro Router | 20 | Flexihopper facing Duero | 20 |  | 10 |  | 10 | RTN facing Anda Candabong Main | Emerson | 53.5V | 0.0A | 16.0A | 16.0A | 3 | 2 | Narada | 155 | Narada | 155 |  |  |  |  | No |  | 53.6V | 53.6V |  |  | OK | 6 | DC Fan | 40 | Harris facing Gorda RS A | 16 | RTN facing Anda Candabong Rdnt | 16 | RTN facing Gorda RS | 40 | Harris DCPDB A | 6 |  | 50 | RTN facing Anda Rdnt | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | BAU | [33 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25 | 70 | Eltek 1 | 70 | Eltek 2 | 50 | Spare | 50 | Emerson | 40 | Spare | 40 | Spare | 40 | TVSS | 40 | Spare | 30 | Van Lights | 30 | Outlet | 30 | ACU 1 | 30 | ACU 2 | 20 | Van Lights | 20 | Outlet | [12 empty] | Done | OK
3386 Corella_3_09_17.pdf | 3386 | CORELLA | 2017-03-09 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | OK | No ATS is installed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Corella, Bohol | Residential | Lot | Permanent | Lot | 3L-SST and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Leonarda Manluza | 9183224382 | 123° 55’ 23.3” | 09° 41’ 11.6” | Brgy. Poblacion, Corella, Bohol | 2017-01-01 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-06-02 | OK | Ok | None | OK | OK | For CSMP Endo | For rehab of the roof | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDB15PC-0167137 | 51QSXRACCON19KEDB15PC-0167177 |  | Working | Working | Off | 7.2A | 7.0A |  |  |  | 2000-01-01 | None | None | Shinsetsu | None | None | 10 | Working | Off | 469 | None |  | Defective | None | 8 inches | 2424010353 | Working | N/A | None |  |  | Off | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 8059.02 | 7747.7 | -33 | OK | OK | No | 815-Tagbilaran 1 | Huawei | RTN 950 | No | 8059.02 | 7747.7 | -34 | OK | OK | No | V0008-Sikatuna |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Tagbilaran 1 | 1 |  | 2 | Sikatuna 2G-900 1st E1 | 3 |  | 4 |  |  |  | 7 | Corella 2G-900 1st E1 | facing Sikatuna | 1 | Sikatuna 2G-900 1st E1 | 2 |  | 3 |  | 4 | [18 empty] | facing Tagbilaran 1 | 1 | Corella 3G-2100 | 2 | Sikatuna 3G-2100 | 3 |  | 4 | [13 empty] | facing Sikatuna | 1 | Sikatuna 3G-2100 | [49 empty] | Eltek | 54.25V | 0.0A | 32.0A | 32.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.4V | 54.4V | 54.4V | 54.4V | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G-2100 DCDU 12B | 40 |  | 40 |  | 40 |  | 40 |  | 40 | 3G-2100 BBU | 20 | RRU 0 | 20 | RRU 1 | 20 | RRU 2 | 16 | Hopper facing Sikatuna | 16 | RTN facing Sikatuna Main | 80 | RTN facing Sikatuna Rdnt | 80 | BTS 3900L Upper 23. BTS 3900L Lower | [15 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 |  | 70 | ELTEK 2 | 70 | ELTEK 1 | 30 | ACU 1 | 30 | ACU 2 | 30 | SPARE | 30 | SPARE | 20 | LIGHTINGS | 20 | C.O. | 20 | SPARE | 20 | TOWER LIGHT | [20 empty] | Off | Off |  |  |  | Rectifier Cabinet | 1 unit | APM 200 / SN: | WFM, FO | [36 empty] | Civil | Cabin Roof/Ceiling | 1 Lot | [88 empty] | Roof/ceiling for rehab
4200 Loon RS_2_24_17.pdf | 4200 | LOON RS | 2017-02-24 | FHG/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK | See attached extra page. | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed | N/A | No Bro installed | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Off | Please see page 5 | OK |  | OK |  | OK |  | OK | Kipor genset defective AVR, already requested. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Tanawan, Loon, Bohol | Residential | Lot | Permanent | Lot | 4L-SST / 120 Ft. | Collapsible | 24 Hrs. | Security Guard | Yes |  | Paulina Cartagena |  | 123° 48’ 51” | 09° 46’ 40” | Brgy. Tanawan, Loon, Bohol | 36586 | For Repair | for CSMP Endo | for Replacement | OK |  | Working | OK | OK | For Rehab | OK | OK | OK | For Rehab | OK | OK | 42979 | OK | Ok | 0 / 1 | OK | OK | OK |  | WACU | WACU | WACU | WCONX019ED1 | WCONX019ED1 | FP-51QSXRACCON19KEDP1C | 51QSXRACCON19KEDJ13PC-0317996 | 51QSXRACCON19KEDJ13PC-0317934 | 51QSXRACCON19KEDH08PC-0477879 | Working | Working | Working | 7.2A | 7.0A | 7.1A |  |  | 42736 | Off | Off | DENYO, KIPOR | Off | Off | 45, 60, | Off | Off | 941.9, 290.6 | Off |  | Defective | Off |  | 707091034 | Working |  | Working | ACU 4: Model: WCONX019ED1, SN: 51QSXRACCON19KEDJ12PC-0384313, Working, 7.2A. Defective AVR of Kipor Genset, already requested. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Nokia | Flexihopper | Yes | 1507.5 | 1465.5 | -37 | OK | OK | No | 3307-Loon TP | Aviat | Harris Stratex | Yes | 7316.75 | 7373.25 | 0.90535 | OK | OK | Yes | 5405-Loon Catagbakan | Huawei | RTN 950 | No | 7762.53 | 8073.85 | -35.3 | OK | OK | Yes | 3311-Catigbian |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | NE40E-X2 | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off | See attached PD File for MW and RSLs for SDH | Hauwei NE40E-X2 | 1 | RTN NMS via TDM | 2 | to Port 3 of Harris Catagbakan | 3 |  | 4 |  | 5 |  | 6 |  | Huawei NE40E-X2 Expansion | 0/7/0 | Loon RS 2G 1st E1 | [23 empty] | Hauwei NE40E-X2 0/2 | 1 |  | 2 | Loon RS WCDMA | 3 |  | 4 |  | 5 |  | 6 | Catigbian 3G Clauster | 7 | HCEN Resiliency | 8 | Pitogo Bro |  |  |  |  | Hauwei NE40E-X2 0/6 | 1 |  | 2 |  | 3 |  | 4 |  | 5 | HCEN Resiliency | 6 |  | 7 |  | 8 | Catigbian NMS |  |  |  |  | 42737 | to Loon Catagbakan | 13.1 KM | 42924 | to SUN Loon Cogon Sur | 4.610KM | [25 empty] | Eltek | 53.83V | 0.0A | 51.0A | 51.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.9V | 53.9V | 53.9V | 53.9V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 | NEC DCPDB B | 63 | FUJITSU DCPDB1 B | 63 |  | 63 |  | 63 |  | 40 | SMART CEN REDUNDANT | 40 | FUJITSU DMGTE DCPDB B | 40 | FUJITSU PANGLAO DCPDB B | 40 | FUJITSU CAMANGAY B | 40 |  | 40 | WCDMA | 20 |  | 20 |  | 20 | RTN 950 facing Catigbian Main | 16 | ECI MUX B | 16 | CATAGBAKAN HARRIS B | 16 | LOON TP HOPPER | 16 |  | Eltek | 53.81V | 0.0A | 26.0A | 26.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.8V | 53.8V | 53.8V | 53.8V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 | FUJITSU DCPDB1 B | 63 | NEC DCPDB BRANCH A | 63 |  | 63 |  | 63 |  | 40 | FUJITSU CAMANGAY A | 40 | FUJITSU PANGLAO DCPDB A | 40 | FUJITSU DMGTE DCPDB A | 40 | SMART CEN A | 40 |  | 40 |  | 20 |  | 20 |  | 20 | RTN 950 facing Catigbian Rednt | 16 | ECI MUX A | 16 | CATAGBAKAN HARRIS A | 16 | LOON TP HOPPER | 16 | DC FAN | Eltek | 54.21V | 0.0A | 14.0A | 14.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.3V | 54.3V | 54.3V | 54.3V | OK | 100 |  | 100 |  | 100 | BTS 3900L UPPER | 100 | BTS 3900L LOWER | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | 100 | 49.5 | 70 | ELTEK B2 | 70 | SPARE | 50 | TVSS | 50 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | ACU 1 | 30 | ELTEK A2 | 30 | ELTEK A1 | 30 | SPARE | 30 | ACU 2 | 20 | LIGHTINGS | 20 | OUTLET |  |  | 70 | ELTEK B1 | [8 empty] | Done | OK | [43 empty] | Civil | Shelter Flooring | 1 Lot | [83 empty] | Old Cabin | New Cabin |  |  |  | New cabin flooring for rehab
4209 Garcia Hernandez_2_6_17.pdf | 4209 | GARCIA HERNANDEZ | 2017-02-06 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | 3G xml | OK | -40.8/-34.8 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek 1: 54.1V, 54.1V, 54.1V, 54.1V Eltek 2: 54.7V, 54.7V, 54.7V, 54.7V | OK | Passed. | N/A |  | OK |  | OK | Defective ATS, already requested. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion East. Garcia Hernandez, Bohol | Residential | Lot | Permanent | Lot | Guyes Tower / 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Dr. Mavil Lim | 9177249327 | 124° 17’ 40” | 09° 36’ 51” | Brgy. Poblacion West, Garcia Hernandez, Bohol | 2017-03-01 | For Repair | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 2000-06-01 | OK | Ok | 2000-01-01 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDP3C | WCONX019ED1 |  | 51PMXRACCAR19KEDN07PC-0376633 | 51QSXRACCON19KEDK13PC-0356988 |  | Working | Working | Off | 7.8A | 7.1A |  |  |  | 2000-01-01 | None | None | Denyo | Defective | None | 45 | Working | Off | 1698.6 | None | 2003-002538 | Defective | None | 200 | 02-0291--0070 | Working | N/A | Working | Ongoing construction of genset pad and fuel tank pedestal. |  | Off | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Aviat | Harris Stratex | Yes | 7470.5/7762.525 | 7638.5/8073.845 | -40.8/-34.8, -41.1 | OK | OK | Yes | 3336-Laka RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 |  | 2 |  |  | See attached PDF for E1 inventory | [6 empty] | Harris facing Laka RS | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 | [14 empty] | Huawei CEN | [7 empty] | See attached inventory for FE inventory | [12 empty] | Harris facing Laka RS | 1 |  | 2 |  | 3 |  | 4 | [44 empty] | Eltek #1 | 54.55V | 0.0A | 11.0A | 11.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.1V | 54.1V | 54.1V | 54.1V | For Rectification | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3336 Laka RS A | 40 | NE40E-X2-M8 Main | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | Eltek #2 | 54.0V | 0.0A | 25.0A | 25.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.7V | 54.7V | 54.7V | 54.7V | Off | 100 | BTS 3900L Upper | 100 | BTS 3900L Lower | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G-2100 DCDU | 40 | NE40E-X2-M8 Rdnt | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | 3336 Laka RS B | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25 | 70 | Eltek 1A | 70 | ELTEK 2A | 50 | Eltek 2B | 50 | Eltek 1B | 40 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 30 | Tower Light | 30 | Tower Light | 30 | ACU 1 | 30 | ACU 2 | 20 | Lightings | 20 | C. O. | [12 empty] | Done | OK | [43 empty] | Civil | Others (Shelter Flooring) | [89 empty] | For floor rehab.
4210 Valencia.pdf | 4210 | Valencia | 2017-03-06 | RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Juan C. Pajo Ave., cor Savero Pajo St., Brgy. Poblacion Occ., Valencia, Bohol | Residential | Lot | Permanent | Lot | SST 150ft | Room | 24hrs | Caretaker | Yes |  | Catholic Bishop Tagbilaran |  | 124°12'28.80"E | 9°36'32.04"N | Juan C. Pajo Ave., cor Savero Pajo St., Brgy. Poblacion Occ., Valencia, Bohol | 2,1 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 8,0 | OK | Ok | 0,1 | OK | OK | Off |  | WACU | WACU | Off | WCONX019ED1 | WCONH019ED |  | 51QSXRACCON19KEDT15PC-0722272 | 51QSXRACCON19KEDT16PC-1074497 |  | Working | Working | None | 5.6 | 7.5 |  |  |  | 1,0 | None | None | POWERCITY | Working | None | 25 | Working | Off | 179.2 | None | 2003-002540 | Working | None | 17 inches |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | AVIAT |  | Yes | 7317 | 7121 | 0.88095 | OK | OK | Yes | GORDA RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40E | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI CEN | 0/4/1 | GUINDULMAN 2G 1ST E1 | 0/4/2 | GUINDULMAN 2G 2ND E1 | 0/4/3 | CANDIJAY 2G 1ST E1 | 0/4/4 | CANDIJAY 2G 2ND E1 | 0/4/5 | MABINI 2G 1ST E1 | 0/4/6 | MABINI 2G 2ND E1 | HUAWEI CEN | 0/4/7 |  | 0/4/8 | VALENCIA 2G 1ST E1 | 0/4/9 | VALENCIA 2G 2ND E1 | [19 empty] | HUAWEI CEN | 1 | VALENCIA 3G | 2 | ANDA AND ANDA CANDABONG 3G | [16 empty] | AVIAT | 2 | ANDA AND ANDA CANDABONG 3G | [18 empty] | 1 & 2 | 0/2/0 (FACING GARCIA HERNANDEZ) | 11.41 | 7 & 8 | 0/6/0 (FACING DIMIAO) | 6.18 | [25 empty] | ELTEK | 54 | 0 | 5 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.4 | 53.3 | 53.3 | 53.2 | OK | 100 | PLDT DCPDB 1 | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 | HUAWEI CEN B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | AVIAT GORDA B | 16 |  | 16 |  | 16 |  | EMERSON | 54.5 |  | 45 |  | 3 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 51.8 | 51.7 | 51.6 | 51.5 | OK | 6 |  | 6 |  | 16 |  | 16 |  | 40 | AVIAT GORDA A | 40 | HUAWEI CEN A | 80 | BTS3900L UPPER | 80 | BTS3900L LOWER | 50 | 3G WCDMA | 50 |  | 50 |  | 50 |  | 6 | [34 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 22 | 70 | ELTEK RECTIFIER 1 | 70 | EMERSON RECTIFIER | 40 | ACU 1 | 40 | ACU 2 | 20 | VAN LIGHTS | 20 | C.O. | 20 | TOWER LIGHT | 20 | PERIMETER LIGHT | 70 | ELTEK RECTIFIER 2 | [22 empty] | Done | OK |  |  |  | NOKIA EMPOWER RECTIFIER | 1 | SN:2256808 | FO & WFM | BATTERIES | 8 | NARADA 12V/155AH | FO & WFM | [32 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING | 1
4211 Guindulman_3_22_17.pdf | 4211 | GUINDULMAN | 2017-03-22 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G & LTE TDD xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5 | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Sitio Baud, Brgy. Tabahan, Guindulman, Bohol | Residential | Lot | Permanent | Lot | 3L-SST and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Dr. Rolando Salada | 9391495011 | 124° 29’ 0” | 9° 45’ 45” | Sitio Baud, Brgy. Tabahan, Guindulman, Bohol | 36617 | OK | for CSMP Endo | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 36739 | OK | Ok | 0 / 1 | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | FP-51QSXRACCON19KEDP1C |  | 51QSXRACCON19KEDJ13PC-0317912 | 51QSXRACCON19KEDH10PC-0354590 |  | Working | Working | Off | 7.0A | 7.1A |  |  |  | 36526 | None | None | Denyo | Working | None | 25 | Working | Off | 1938 | None | 2003-002541 | Working | None | 11.5 inches | 05-0591-0080 | Working | N/A | Working |  | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off | Boser | 6 | Retrieved | None |  | Off | BBU 3900 | Retrieved |  | Off | Normal status | OK | OK | Aviat | Harris Stratex | Yes | 7681.00, 8073.845 | 7513.00, 7762.525 | -36.4/-39.3, -34, -33 | OK | OK | Yes | 3336-Laka RS | Aviat | Harris Stratex | Yes | 7625 | 7457 | 0.86534 | OK | OK | Yes | 4212-Candijay |  |  | Yes |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | Guindulman-Laka Freq. 8133.145 / 7821.825 | facing Laka RS | 17 | Guindulman 2G 1st E1 | 18 | Guindulman 2G 2nd E1 | 19 | Candijay 2G 1st E1 | 20 | Candijay 2G 2nd E1 | 21 | Mabini 2G 1st E1 | 22 | Mabini 2G 2nd E1 | facing Candijay | 1 | Candijay 2G 1st E1 | 2 | Candijay 2G 2nd E1 | 3 | Mabini 2G 1st E1 | 4 | Mabini 2G 2nd E1 | [17 empty] | facing Laka RS | P1 | Guindulman TD LTE DAC GE3 Slot 2 | P2 | Guindulman Bro DAC ES | P2 | 3G (Mabini&Candijay) DAC GE3 Slot5 | [14 empty] | facing Candijay | 2 | 3G-2100 (Mabini&Candijay) DAC GE Slot2 | [49 empty] | Eltek | 54.02V | 0.0A | 49.0A | 49.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.2V | 53.2V | 53.2V |  | Off | 100 | DFB A | 100 | BTS 3900L Lower | 100 |  | 100 |  | 63 | 3G-2100 DCDU 12B | 63 | LTE-TDD | 63 |  | 63 |  | 63 |  | 40 | DCPDB A | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | ZTE | 53.5V | 0.0A | 3.0A | 3.0A | 3 | 2 | Lynx | 170 | Lynx | 170 |  |  |  |  | No |  | 52.4V | 52.4V |  |  | OK | 100 | DFB B | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 40 |  | 40 |  | 40 |  | 40 | DCPDB B | 16 |  | 16 |  | 16 |  | 80 | [24 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 23 | 70 | Eltek 1 | 70 | ZTE | 50 | Eltek 2 | 50 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | CB ACU-DTS | 30 | SPARE | 30 | ACU 1 | 30 | ACU 2 | 20 | LIGHTING | 20 | C. O. | [12 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 unit | Nokia Empower / SN: | WFM, FO | Rectifier Batteries | 12 pcs | Narada / 155AH, 12V | WFM, FO | [32 empty] | Civil | Roofing | 1 Lot |  |  |  |  | Civil | Flooring | 1 Lot | [81 empty] | Flooring and roofing for rehab.
4212 Candijay_3_22_17.pdf | 4212 | CANDIJAY | 2017-03-22 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5 | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | San Antonio St., Brgy Poblacion, Candijay, Bohol | Residential | Lot | Permanent | Lot | 3L-SST and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Florencio Bayron | 9214622505 | 124° 0’ 08” | 09° 51’ 14” | San Antonio St., Brgy Poblacion, Candijay, Bohol | 0 / 4 | OK | for CSMP Endo | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36739 | OK | Ok | None | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDK12PC-0416758 | 51QSXRACCON19KEDK12PC-0416758 |  | Working | Working | Off | 7.0A | 7.2A |  | Already covered. | Already covered. | 36526 | Defective | Defective | Denyo | Working | None | 25 | Working | Off |  | None | 2003-002537 | Working | None | 12 inches | 07-0791-0035 | Working | N/A | Working |  | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off | Boser | 6 | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Aviat | Harris Stratex | Yes | 7457 | 7625 | 0.88776 | OK | OK | Yes | 4211-Guindulman | Aviat | Harris Stratex | Yes | 7177 | 7373 | 0.88989 | OK | OK | Yes | 4329-Mabini | Aviat | Harris Stratex | Yes |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Guindulman | 1 | Candijay 2G 1st E1 | 2 | Candijay 2G 2nd E1 | 3 | Mabini 2G 1st E1 | 4 | Mabini 2G 1st E1 |  |  |  |  | facing Mabini | 1 | Mabini 2G 1st E1 | 2 | Mabini 2G 1st E1 | 3 |  | 4 | [18 empty] | facing Guindulman | 1 |  | 2 | Mabini 3G-2100 | 3 | Candijay 3G-2100 | 4 | [13 empty] | facing Mabini | 1 |  | 2 |  | 3 |  | 4 | [43 empty] | Nodal Aviat | Empower | 56.19V | 0.0A | 35.3A | 35.3A | 6 | 2 | Hawker | 300 | Hawker | 300 | Hawker | 300 |  |  | No |  | 52.1V | 52.0A |  |  | OK | 40 | 4211 Guindulman Harris A | 40 | 4211 Guindulman Harris B | 40 | 3G-2100 DCDU 12B | 40 |  | 16 | 3G-2100 DCDU 12B | 16 | LTE-TDD | 16 |  | 16 |  | 16 |  | 6 | DCPDB A |  |  | 80 | BTS 3900l Upper | 80 | BTS 3900l Lower | 6 |  | 6 |  | 100 |  | 100 | [11 empty] | Eltek |  | 0.0A |  |  | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.1V | 53.1V | 53.1V | 53.1V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 27 | 70 | EMPOWER | 70 | Eltek 1 | 50 | SPARE | 70 | Eltek 2 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | LIGHTING | 30 | ACU 1 | 30 | PERIMTER | 30 | ACU 2 | 20 | TOWER | 20 | C. O. | [12 empty] | Done | OK |  |  |  | Rectifier Cabinet | 2 units | Emerson 48420 | WFM, FO | [36 empty] | Civil | Roofing | 1 Lot | [88 empty] | Roof for repair
4213 Loay_2_28_17.pdf | 4213 | LOAY | 2017-02-28 | FHG/RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK | See page 4. | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed. | N/A | No Bro installed. | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK | Passed. | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Loay, Bohol | Residential | Lot | Permanent | Lot | 3L-SST / 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Gertrudes Bernaldez | (038) 538-9015, 09295249639 | 124° 00’ 46.2” | 09° 35’ 59.1” | Brgy. Poblacion, Loay, Bohol | 36557 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36678 | OK | Ok | 0 / 0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | FP-51PMXRACCARP19KEDP3C |  | 51QSXRACCON19KEDM14PC-0516821 | 51PMXRACCAR19KEDT07PC-0500859 |  | Working | Working | Off | 8.1A | 7.9A |  |  |  | 36526 | Off | Off | DENYO | Working | Off | 25 | Working | Off | 9656.3 | None | 12620708 | Working | None | 360 | 1515010966 | Working | N/A | Working | Exhaust fan were already converted and covered with plain sheet. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 620 | No | 14907 | 15327 | -36.2 | OK | OK | No | 4328-Loboc | Ericsson | Minilink TN | Yes | 8307 | 8426 | -39.1 | OK | OK | Yes | V0118-SUN Panglao 3 | Aviat | Harris Stratex | Yes | 7457 | 7625 | 0.91221 | OK | OK | Yes | 815-Tagbilaran 1 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | CEN NE40E-X2 | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | RTN facing Loboc | 1 |  | 2 |  | 3 | See attached PDF for E1 inventory | 4 |  | 5 |  | 6 |  | Harris facing Tagbilaran 1 | [5 empty] | See attached PDF for E1 inventory | [6 empty] | Ericsson facing SUN Panglao 3 | [5 empty] | See attached PDF for E1 inventory | [6 empty] | RTN facing Loboc | 1 |  | 2 |  | 3 | See attached PD file | 4 | [13 empty] | Harris facing Tagbilaran 1 | [51 empty] | Eltek | 53.92V | 0.0A | 44.0A | 44.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 52.4V | 52.9V | 52.8V | 52.7V | OK | 80 | BTS 3900L UPPER | 16 |  | 80 | BTS 3900L LOWER | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | HARRIS DCPDB A | 40 | WCDMA | 40 | NE40E-X2 MAIN | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | ERICSSON MLTN 6P B | 16 |  | 16 |  | 16 |  | Emerson | 53.5V | 0.0A | 0.0A | 0.0A | 3 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 52.4V | 52.3V | 52.3V |  | Off | 6 |  | 6 | RTN 950 FACING SEVILLA B | 16 | RTN 950 FACING LOBOC B | 16 | ERICSSON MLTN 6P A | 40 | HARRIS DCPDB B | 40 | NE40E-X2 REDUNDANT | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | [34 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 30.6 | 70 | ELTEK 1 | 70 | EMERSON | 50 | ELTEK 2 | 50 | ACU 2 | 40 | SPARE | 40 | ACU 1 | 40 | SPARE | 40 | C. O. | 30 | SPARE | 30 | TOWER LIGHT | 30 | PERIMETER LIGHTS | 30 | SPARE | 20 | LIGHTINGS | 60 | SPARE | [12 empty] | Done | OK |  |  |  | WACU | 1 UNIT | CONDURA, 2HP / 048406019 | WFM, FO | RECTIFIER | 1 UNIT | NOKIA EMPOWER / S.N.: 2291910 | WFM, FO | [32 empty] | Civil | Others (Shelter Flooring) | 1 Lot |  |  |  |  | Civil | Others (Cabin Wall) | 1 Lot | [81 empty] | Floor and cabin wall for rehab
4215 Tayasan (1st Half) 2017v2-.pdf | 4215 | Tayasan | 2017-01-31 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - BLA07386203 (Tayasan facing Guihob) Aviat ODU4 - BLA07386123 (Tayasan facing Guihob) Aviat ODU2 - EBT1209B298 (Tayasan facing Guihob) Aviat ODU5 - EBT1150C291 (Tayasan facing Guihob) Aviat ODU1 - EBT07220247 (Tayasan facing Bindoy) Aviat ODU4 - EBT07220254 (Tayasan facing Bindoy) Aviat ODU2 - EBT1151A190 (Tayasan facing Bindoy) Aviat ODU5 - EBT1125K106 (Tayasan facing Bindoy) Aviat ODU2 - EBT1102A077 (Tayasan facing Jimalalud) Aviat ODU5 - EBT1102A133 (Tayasan facing Jimalalud) Aviat ODU1 - a23105mh5s (Tayasan facing Ayungon) Ericsson TN | OK |  | N/A |  | OK |  | OK |  | Rectification | ODU1/4 -38.9 / -45.2 (Tayasan facing Guihob) Aviat , for fine tuning ODU2/5 -41.8 / -46.4 (Tayasan facing Guihob) Aviat , for fine tuning ODU1/4 -25.3 / -27.2 (Tayasan facing Bindoy) Aviat ODU2/5 -37.9 / -30.9 (Tayasan facing Bindoy) Aviat ODU2/5 -40.3 / -43.4 (Tayasan facing Jimalalud) Aviat ODU1 -36.3 (Tayasan facing Ayungon) Ericsson TN | OK |  | OK | NOC PMR Ctrl# 17Q1-0455 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | defective auto start with genset | OK |  | OK | TX facing 5861 Mt Guihob needs fine tuning | OK |  | OK |  | OK |  | AECabral III | B | Jan 30 2017 | Callao St. Brgy Poblacion, Tayasan, Negros Oriental | Low land | within premise | Commercial | Stand by | guyed tower 150ft | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | JONATHAN A. LUZURIAGA |  | 123.1736 | 9.9226 | Callao St. Brgy Poblacion, Tayasan, Negros Oriental | ok | For Repair | OK | OK | For CSMP Endo | for grass cutting | Working | OK | For Repan/Reloc | OK | OK | OK | OK | OK | OK | OK | some busted light | OK | Ok | none | OK | OK | For CSMP Endo | shelter floor needs cleaning | WACU | WACU | Off | fp-51qsxracc0nr19kedp1c | wconx019ed1 |  | 51qsxraccon19kedn10pc-0470271 | 51qsxraccon19ked b15pc-0154333 |  | Working | Working | Off |  |  |  | for condemn | for condemn | WORKING but defective auto | Off | Off | Denyo | Defective | None | 25 KVA | Working | CF100 | working | None | 72346159 | Working | None |  |  | Working |  | Working | Defective auto in genset, ATS is OK | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Aviat | Stratex | Yes | 7240 | 7401 | 0.86062 | OK | OK | Yes | 5861 Mt Guihob | Aviat | Stratex | Yes | 7373 | 7177 | 0.93015 | OK | OK | Yes | 4216 Bindoy | Aviat | Stratex | Yes | 7681 | 7513 | 0.92857 | OK | OK | Yes | 4260 Jimalalud | Ericsson | Minilink TN | No | 8363 | 8482 | -36.3 | OK | OK | No | V4386 Ayungon |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Aviat facing Mt Guihob | 1 | Mt Guihob 2G | 2 | Guihulngan GSM | 3 | Guihulngan DCS | 6 | Guihulngan Cruztelco 1st E1 | 12 | La Libertad 2G | 6 | 2G 2nd E1 | [26 empty] | Aviat facing Bindoy | s3-p1 | DPP for link 2 | s3-p2 | DPP for link 2 | s3-p3 | Guihulngan & La Libertad WBB (BRO) | s3-p4 | Guihulngan 3G | s3-p5 | Tayasan 3G (via DAC GE from Jimalalud Node) | [10 empty] | Aviat facing Mt Guihob | s6-p1 | DPP for link 2 | s6-p2 | DPP for link 2 | s6-p3 | Guihulngan & La Libertad WBB (BRO) | s6-p4 | Guihulngan 3G | s6-p5 | [12 empty] | Aviat facing Jimalalud |  | s6-p1 |  |  | s6-p2 | Tayasan and Jimalalud 3G |  | s6-p3 | Tayasan 3G |  | s6-p4 | [18 empty] | Eltek Valere | 54.65 | 0 | 39 | 39 | 4 | 3 | SacredSun | 180 | SacredSun | 180 |  |  |  |  | No |  | 54.2 | 53.8 | 54 |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 | 2G BTS3900L lower | 80 | 2G BTS3900L upper | 80 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | DCPDB Main | 40 |  | 40 |  | 40 | Tayasan 3G DCDU | 20 |  | 20 |  | 20 |  | 20 |  | 10 |  | 10 | RTN950 Facing Ayungon | Nokia EMPower 1100 | 54.34 | 0 | 4.7 | 4.7 | 5 | 3 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 |  |  | No |  | 53.5 | 53.6 | 54 |  | OK | 40 |  | 40 |  | 40 |  | 40 |  | 40 | DCPDB Protect | 16 |  | 16 |  | 16 |  | 16 | RTN950 Facing Ayungon | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 80 |  | 100 | [26 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 22 | 70 | EmPower | 70 | Eltek | 50 |  | 50 |  | 40 |  | 40 |  | 40 |  | 40 |  | 30 |  | 30 | ACU | 30 | Perimeter lights | 30 | ACU | 20 | Cabin lights | 20 | C.O. | [12 empty] | Done | OK |  | AECabral III | 42765 | Batteries | 8 | Ritar 150 | WFM | Batteries | 4 | PowerSafe 155 | WFM | Batteries | 4 | Leoch 150 | WFM | [28 empty] | ELECTROMECHANICAL | Radio lightings | 2 | n.a. | n.a. | 20watts |  |  | GENSET | 1 |  |  |  | for automatic start
4216-BINDOY-031617.pdf | 4216 | Bindoy | 2017-03-16 | rdcueco | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK | 17Q1-1579 | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | dilapidated floor | OK |  | OK |  |  | B |  | Poblacion Bindoy Negros Oriental | Commercial | Lot | Permanent | Lot | 150 ft SST | Van | 24 hrs | Caretaker | Yes | [7 empty] | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | For Rehab |  | OK | For Rectification | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019EA1 |  | 540014 | H12PC0344442 |  | Working | Working | Off |  |  |  | NA | NA |  | Off | Off |  | Working | None |  | Working | CF100 |  | Working |  | None | None |  |  | Working |  | Working |  | HUAWEI | Off | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off | NA | Off | NA |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | ERICSSON | MLTN | No | 15327 | 14907 | -38 | OK | OK | No | V3662 SUN BINDOY | HARRIS |  | Yes | 7177 | 7373 | 1.2222 | OK | OK | Yes | 4215 TAYASAN | HARRIS |  | Yes | 7513 | 7681 | 0.86486 | Off | Off | Yes | SAMBOAN |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | NOKIA | 55.62 | 0 | 0 |  | 5 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No | [5 empty] | OK | 40 |  | 40 |  | 40 | 3G | 40 | HARRIS DCPDB MAIN | 40 |  | 16 | ALLIED TURBO SWITCH |  |  | 80 | BTS UPPER | 16 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 100 | BTS LOWER | 100 | [11 empty] | NOKIA | 54.78 |  | 2 | 2.4 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | Off | [5 empty] | OK | 40 | HARRIS DCPDB PROTECT | 16 |  | 40 |  | 16 |  | 16 |  | 80 |  |  |  | 40 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 10 |  | 100 |  | 100 | [26 empty] | Off | [5 empty] | Off | [44 empty] | 100 |  | 70 | NOKIA ACCESS LOAD | 70 | NOKIA TX LOAD | 50 |  | 50 |  | 40 |  | 40 |  | 40 |  | 40 | PERIMETER LIGHT | 30 | TOWER LIGHT | 30 | ACU 1 | 30 | TVSS | 30 | ACU 2 | 20 | VAN LIGHT | 20 | CO | [12 empty] | Done | OK
4217 Bacong First Half 2017 PMR v2.pdf | 4217 | BACONG | 2017-02-09 | KTA / RDC | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | AWAITING SPARE AVAILABILTY FOR ELTEK RM | OK |  | OK |  | OK |  | Rectification | GENSET NOT IN AUTO MODE - NEW ATS FOR INSTALLATION | OK |  | OK |  | Rectification | CABIN NEEDS FLOORING REHAB | OK |  | OK |  |  | A |  | LOWER BUNTIS, BACONG, NEGROS ORIENTAL | RESIDENTIAL | GREENFIELD | PERMANENT | LOT | SST / 42M | VAN | 24/7 | CARETAKER | Yes |  | FELICISIMA AUSEJO LUNA | 9183224755 |  |  | LOWER BUNTIS, BACONG, NEGROS ORIENTAL | 2017-03-01 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 2017-03-08 | OK | Ok | 0/1 | OK | OK | OK |  | WACU | WACU | Off |  | FP-51PMXRACCARP19KEDP3C |  | 51QSXRACCON19KED T15PC - 0725386 | 51PMXRACCAR19KED N09PC - 0437237 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | 2017-01-01 | None | None | DENYO | Defective | None | 25 | Working | CF100 | 8648 | Working | 2264306 | Working | None | 2000 Li |  | Working | 0 | None |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off | BOSER | 2 | Retrieved | None |  | Off | BBU3900 | Retrieved |  | Off |  | OK | OK | HARRIS | STRATEX | Yes | 13171 | 12905 | 0.92857 | Off | Off | Yes | 5427 BANILAD | HARRIS | STRATES | Yes | 7324 | 7163 | 0.92252 | Off | Off | Off | 811 DUM1 | HARRIS | STRATEX | Yes | 7401 | 7240 | 0.90887 | OK | Off | Yes | V4258 SUN DAUIN | HUAWEI | RTN9550 | Yes | 12905 | 13171 | 0.87745 | Off | Off | Off | V5079 DAUIN SAN MIGUEL |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | FS | Yes | Trad | Yes | ECI | FS | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | NOKIA | 54.24 | 0 | 44.5 | 44.5 | 5 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 |  |  | No |  | 53.5 | 54.4 | 54.3 |  | OK | 40 | DCPDB A |  |  | 40 | 3G U2100 | 40 | LTE TDD | 40 | VAPEL A | 16 | INVERTER | 16 | RTN950 F V5079 DAUIN SAN MIGUEL | [10 empty] | 6 | TELLABS 8620 PROTECTION |  |  |  |  | 80 | BTS3900L | [12 empty] | ELTEK | 53.99 | 1 | 3 | 3 | 2 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.5 | 53.4 |  |  | OK | [14 empty] | 40 | DCPDB B | 40 | RTN950 F V5079 DAIUN SAN MIGUEL | [26 empty] | NOKIA | 54.8 | 0.1 | 0 | 2 | 2 | 2 | RITAR | 150 | RITAR | 150 |  |  |  |  | No |  | 54.2 | 54.6 |  |  | Off | [10 empty] | 40 | VAPEL B | [6 empty] | 80 | BTS3900L LOWER | [24 empty] | 100 | 100 | 70 | EMPOWER 1100 | 50 | ELTEK 1 | 40 | PSSS RECTIFIER | 50 | TOWER LIGHT | 30 |  | 40 | TVSS | 30 |  | 40 | ELTEK 2 | 30 | ACU1 |  |  | 30 | ACU2 |  |  | 20 | LIGHTINGS |  |  | 20 | CO |  |  | 40 | P.L. |  |  |  | VACANT |  |  | Done | OK |  |  |  | BATTERY | 12 | NARADA AG12V155F | WFM | BATTERY | 4 | RITAR RA12-150 | WFM
4249 Baclayon.pdf | 4249 | Baclayon | 2017-02-08 | RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK | -34 | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek 1=54.70V;25A Eltek 2=54.09V;14A | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | B |  | Jacinto St. Brgy Poblacion, Baclayon, Bohol | Residential | Lot | Permanent | Lot | Guyed, 150 ft. | Room | 24 | Caretaker | Yes |  | BLESILA LUISA D. CUARTEROS |  | 123°54'21.60"E | 9°37'27.84"N | POBLACION BACLAYON, BOHOL | 3,1 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 5,0 | OK | Ok | 0,1 | OK | OK | OK |  | WACU | WACU | Off | FP-51QSXRACCONR19KEDP1C | FP-51QSXRACCONR19KEDP1C |  | 275963 | 529344 |  | Working | Working | None | 1 | 6.5 |  |  |  | 1,0 | None | None | Airman | Working | None | 25 | Working | CF100 | 3465.3 | None | 9651398 | Working | None |  | 1414020777 | Working |  | Working |  |  | Off | Huawei BTS3900L | Retrieved | BBU3900 & RRU | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN950 | No | 14739 | 15159 | -34 | OK | OK | Yes | SUN Baclayon |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | NE40 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 |  | 2 |  | 3 | Baclayon 2G | 4 | SUN Baclayon 2G |  |  |  |  | Huawei RTN | 1 | SUN Baclayon 2G | [23 empty] | Huawei CEN | 1 |  | 2 | SUN Baclayon 3G | 3 |  | 4 |  | 5 | Baclayon 3G | [10 empty] | Huawei RTN | 1 | SUN Baclayon 3G | [49 empty] | Eltek | 54.7 | 0 | 25 |  | 4 | 4 | Lynx | 170 | Lynx | 170 | Lynx | 170 | Lynx | 170 | No |  | 54.6 | 54.6 | 54.6 | 54.6 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 |  | 80 |  | 80 | BTS3900L UPPER | 63 |  | 63 |  | 63 |  | 63 |  | 40 | CEN Power A | 40 | DCDU 12B (3G) | 40 | PLDT MSAN AG | 40 | RTN MAIN | 20 |  | 20 |  | 20 |  | 20 |  | 10 |  | 10 |  | Eltek | 54.09 | 0 | 14 |  | 4 | 3 | Narada | 155 | Narada | 155 | Narada | 155 |  |  | No |  | 54.1 | 54.1 | 54.1 |  | OK | 100 |  | 100 |  | 100 |  | 100 | BTS3900L LOWER | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | CEN Power B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | RTN STANDBY | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 20 | 70 | ELTEK2B | 70 | ELTEK1B | 40 | ACU1 | 40 | ACU2 | 20 | VAN LIGHTS | 20 | C.O. | 20 | TOWER LIGHT | 20 | P. LIGHT | 70 | ELTEK1A | 70 | ELTEK2A | [20 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | 2
4259-DUMAGUETE 7-030917.pdf | 4259 | Dumaguete 7 | 2017-03-09 | rdcueco | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK | NOC control # 17Q1-1413 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | Brgy Bagacay Dumagete City | Commercial | Lot | Permanent | Lot | 120 ft SST | Van | 24 hrs | Roving Guard | Yes | [7 empty] | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | NA | For Rectification | Ok |  | OK | OK | OK |  | WACU | Off | Off | 51qsxracc0n19kedr14pc | 51qsxracc0n19kedn14pc |  | 53204 | 592287 |  | Working | Working | Off |  |  |  | NA | NA |  | Off | Off | KIPOR | Working | None | 28KVA | Working | CF100 |  | Working | 2006-20688 | Working | None |  |  | Working |  | Working |  | HUAWEI | Retrieved | HUAWEI | Off | HUAWEI | Retrieved | HUAWEI | Retrieved | NA | Off | NA |  | Off | None | HUAWEI | Retrieved | HUAWEI | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | No | 7457 | 7625 | 0.97143 | OK | OK | Yes | V0067 PNOC VALENCIA |  |  | Yes |  |  |  | Off | Off | No |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | ECI XDM100 | I5-P10 | 3G | I5-P10 | LTE FDD | I5-P12 | RTN NMS | I5-P15 | ALLIED GIG-E SWITCH NMS | [13 empty] | AOC10-P4 |  | AOC10-P5 | [17 empty] | 42737 |  |  | 15/16 | [27 empty] | ELTEK | 53.85 | 0 | 4 | 4 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No | [5 empty] | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | ECI XDM POWER B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | ECI FS SOURCE A | 16 | HUAWEI RTN 950 MAIN | 16 | ALLIED SWITCH TURBO | 16 |  | ELTEK | 53.85 | 0 | 16 | 16 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | Off | [5 empty] | Off | 100 | BTS UPPER | 100 | BTS LOWER | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 | LTE DCDU | 40 | ECI XDM POWER A | 40 | HUAWEI DC BREAKER | 20 |  | 20 |  | 20 |  | 16 | HUAWEI RTN950 PROT | 16 | ECI FS SOURCE B | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 |  | 70 | ELTEK 1A | 70 | ELTEK 2A | 50 |  | 50 | ELTEK 1B | 40 |  | 40 |  | 40 |  | 40 |  | 30 | PERIMETER LIGHTS | 30 | ACU1 | 30 | TOWER LIGHTS | 30 | ACU 2 | 20 | RADIO ROOM LIGHTS | 20 | CO | 70 | ELTEK 2B | [10 empty] | Done | OK
4260 Jimalalud (1st Half) 2017v2-.pdf | 4260 | Jimalalud | 2017-01-31 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU2 - EBT1102A004 (Jimalalud facing Tayasan) Aviat ODU5 - EBT1102A030 (Jimalalud facing Tayasan) Aviat | OK |  | N/A |  | OK |  | OK |  | OK | ODU2/5 -35.8 / -41.2 (Tayasan facing Jimalalud) Aviat | OK |  | OK | NOC PMR Ctrl# 17Q1-0455 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | defective ATS / with new ATS delivered but not yet installed | OK |  | OK |  | OK |  | OK |  | OK |  | AECabral III | B | Jan 30 2017 | National highway, Brgy Poblacion, Jimalalud, Negros Oriental | Low land | within premise | Commercial | Stand by | guyed tower 150ft | Concrete | 24 / 7 | private lot with gate/fence | Yes | 2017 | ROWENA M. ESTORCO |  | 123.1984 | 9.9777 | National highway, Brgy Poblacion, Jimalalud, Negros Oriental | ok | OK | for CSMP Endo | OK | For CSMP Endo | for grass cutting, barb wire top fence for fixing | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | ok | OK | Ok | none | OK | OK | For CSMP Endo | shelter floor needs cleaning | WACU | WACU | Off | fp-51qsxracc0nr19kedp1c | wconx019ed1 |  | 51qsxraccon19kedc10pc-0203865 | 51qsxraccon19ked b13pc-0053321 |  | Working | Working | Off |  |  |  | for condemn | for condemn | WORKING | Off | Off | Demyo | Defective | None | 25 KVA | Working | CF100 | working | None | 72349464 | Working | None |  |  | Working |  | Working | New ATS delivered for installation, on going genset and fuel tank pad construction | BTS3012 | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | For Rectification |  | Off |  | Off |  | Off | UNO related alarm | OK | OK | Aviat | Stratex | Yes | 7513 | 7681 | 0.86893 | OK | OK | Yes | 4215 Tayasan |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Aviat | 1 | 3G 1st E1 | 2 | 3G 2nd E1 | 3 | 3G 3rd E1 | 4 | 3G 4th E1 | 5 | 2G 1st E1 | 6 | 2G 2nd E1 | [99 empty] | Emerson MFU 48420 | 54 | 0 | 37 | 37 | 4 | 3 | Sacred Sun | 150 | Sacred Sun | 150 | Sacred Sun | 150 |  |  | No |  | 53.2 | 53.4 | 53.3 |  | OK |  |  |  |  | 16 | DCPDB Main |  |  | 80 | 2G BTS3900L upper | 63 | 2G BTS3012 | 63 | 3G | 63 | 2G BTS3900L lower | [28 empty] | Nokia EMPower 1100 | 54.34 | 0 | 0.2 | 0.2 | 4 | 3 | Lynx | 170 | Lynx | 170 | Lynx | 170 |  |  | No |  | 53.5 | 53.6 |  |  | OK | [12 empty] | 16 | DCPDB Protect | [45 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 25 | 70 | EmPower | 20 | Perimeter lights | 20 | Cabin lights | 20 | CO | 20 | Tower lights | 40 | ACU | 40 | ACU | 100 | Emerson | [24 empty] | Done | OK |  | AECabral III | 42765 | Batteries | 16 | NorthStar NSB 100FT | WFM | [36 empty] | Electromechanical | ATS | 1 | Kutai | ATS3BC0225 | 220V | 11921
4289 Tagbilaran HNU.pdf | 4289 | Tagbilaran HNU | 2017-02-08 | RSJ | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Off |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Nokia Empower=54.27V; 37.5A Power One=54.60V; 6.9A | OK |  | N/A |  | OK |  | N/A | No Genset | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | Jose A. Clarin St. Brgy Dampas, Tagbilaran, Bohol | School | Building | Permanent | Building | Guyed, 150 ft. | Room | 24 | Admin/Bldg Security | Yes |  | Holy Name University |  | 123°52'4.80"E | 9°39'2.16"N | Jose A. Clarin St. Brgy Dampas, Tagbilaran, Bohol | None | OK | OK | N/A | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 6,0 | OK | Ok | 0,1 | OK | OK | OK |  | WACU | Off | Off | WCONA019ED | WCONX019EA1 |  | A12PC-0006015 | A13A-0011658 |  | Working | Working | Off | 6.6 | 7.5 |  |  |  |  | Off | Off |  | None | None |  | None | Off |  | None |  | None | Off |  |  | Off |  | Off |  | Huawei BTS 3900L | Off |  | Off | BBU 3900 RRU | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | NE40 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 | HNU 2G 1st E1 | 2 | HNU 2G 2nd E1 | [34 empty] | Huawei CEN | 1 |  | 2 |  | 3 |  | 4 |  | 5 (7/5/4) | HNU 3G | [62 empty] | NOKIA EMPOWER | 54.27 | 0 | 37.5 | 37.5 | 4 | 3 | NARADA | 155 | NARADA | 155 | NARADA | 155 |  |  | No |  | 54.2 | 54.2 | 54.2 |  | OK | 40 |  | 40 | HNU 3G | 40 |  | 40 | HUAWEI CEN B | 80 | BTS3900L LOWER |  |  | 80 | BTS3900L UPPER |  |  | 16 | RRU 2 | 16 | RRU 1 | 16 | RRU 0 | 6 |  | 6 |  | 6 |  | 6 |  | 100 |  | 100 | [11 empty] | Power One | 54.6 | 0.8 | 6.9 | 7.6 | 3 | 2 | PowerSafe | 155 | PowerSafe | 155 |  |  |  |  | No |  | 54.4 | 54.4 |  |  | OK | 50 |  | 50 |  | 63 |  | 63 | Huawei CEN A | 40 |  | 40 |  | 16 |  | 16 |  | 16 |  | 10 |  | 10 |  | 10 |  | 10 |  | 6 |  | 6 |  | 80 | [28 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 22.5 | 70 | Power One | 30 | ACU 1 | 70 | Nokia Empower | 30 | ACU 2 | 20 | C.O. | 20 | Van Light | [28 empty] | Done | OK
4298-PAMPLONA TP-012417.pdf | 4298 | Pamplona TP | 2017-01-24 | rdc/kta | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | prime site.only 1 genset working | Rectification | prime site | OK |  | Rectification | Dilapidated ceiling | OK |  | OK |  |  | B
4325 Danao_3_16_17.pdf | 4325 | DANAO | 2017-03-16 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | N/A | Outdoor site. | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | OK | No ATS is installed. Mobile genset is deployed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Danao, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower and 150 Ft. | N/A, Outdoor site | 24 Hrs. | Caretaker | Yes |  | LGU-Danao | 9303595620 | 124° 13’ 14.1” | 09° 56’ 52.5” | Brgy. Poblacion, Danao, Bohol | 42767 | For Repair | For FASG Endo | for Replacement | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | Off | None | OK |  | OK | Ok |  | OK | OK | Off | Outdoor site, no equipment shelter. | Off | Off | Off | [6 empty] | Off | Off | Off | [5 empty] | 36526 | Off | Off | SDMO | None | Off | 6.5 | Working | Off | N/A | None | 04-250656 | None | None | 69 inches (drum) | 18-1891-0105 | Working | 1 | None | No ATS is installed. Mobile genset is deployed. Outdoor site. |  | Off | BTS 3900A | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 7345 | 7184 | -34 | OK | OK | No | 3312-Camangay RS |  |  | No |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | 3312-Camangay RS | 1 | Danao 2G-900 1st E1 | 2 |  | 3 |  | 4 | [6 empty] | 1 |  | 2 |  | 3 |  | 4 | [18 empty] | 3312-Camangay RS | 1 | Danao 3G-2100 | 2 |  | 3 |  | 4 | [14 empty] | 1 |  | 2 |  | 3 |  | 4 | [44 empty] | Huawei (APM30H) | N/A | N/A | N/A | N/A | 3 | 2 | Shoto | 90 | Shoto | 90 |  |  |  |  | No |  | 50.1V | 50.1V |  |  | OK | 25 | FH facing Camangay RS | 15 | CMUA | 15 | BBU 2G | 15 | DCDU | 15 | BBU 3G | 15 | RRU 0 | 5 | RRU 1 | 15 | RRU 2 | 15 | RTN facing Camangay RS Main | [41 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 60 |  | 20 | Perimeter | 20 | Tower Light | 20 | Outlet | 63 | BTS 3900A | 70 | Eltek 1 | 70 | Eltek 2 | [28 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 unit | APM 200 / SN: 21026200112085B90332 | WFM, FO | [36 empty] | Civil | Pedestrian Gate | 1 Lot | [87 empty] | Mobile genset with drum storage for Diesel. | Misaligned gate after earthquake for repair.
4326 Duero_2_23_17.pdf | 4326 | DUERO | 2017-02-22 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK | -40.6 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed | N/A | No Bro installed | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK | Passed. | N/A |  | OK |  | OK | Genset on manual mode due to def. cranking module, already requested repair. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Itum, Duero, Bohol | Commercial | Lot | Permanent | Lot | Guyed Tower / 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | LGU-Duero / Municipal Treasurer | 9173041533 | 124° 24’ 19.5” | 09° 42’ 35.9” | Market Side, Brgy. San Antonio, Duero, Bohol | 42767 | OK | for CSMP Endo | OK | For CSMP Endo | Gate for repaint | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 36617 | OK | Ok | 0 / 1 | OK | OK | OK | Slight repair on flooring | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDM14PC-0532109 | 51QSXRACCON19KEDN14PC-0558045 |  | Working | Working | Off | 6.8A | 7.0A |  |  |  | 36526 | None | None | DENYO | Working | None | 25 | Working | Off | 238.5 | Off | 2363074 | Working | None | 14 inches | 04-0491-0220 | Working | N/A | Working | Exhaust fans were already converted. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Nokia | Flexihopper | No | 7352 | 7191 | -40.0 dBm | OK | OK | No | 3336-Laka RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Laka RS | 1 | Duero 2G 1st E1 | 2 | Duero 2G 2nd E1 | 3 | Duero 3G 1st E1 | 4 |  | 5 |  | 6 | Duero 3G 2nd E1 | facing Laka RS | 7 | Duero 3G 3rd E1 | 8 | Duero 3G 4th E1 | [94 empty] | Nokia | 54.43V | 0.0A | 33.4A | 33.4A | 5 | 2 | Sacred Sun | 180 | Sacred Sun | 180 |  |  |  |  | No |  | 54.5V | 54.5V |  |  | OK | 50 |  | 50 |  | 50 |  | 50 | MBTS 3G-2100 DCDU |  |  | 80 | BTS 3900L LOWER |  |  | 80 | BTS 3900L UPPER | 16 | RTN facing Laka RS Main | 16 | NOKIA FH | 10 | RTN facing Laka RS Redundant | [37 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25 | 70 | EMPOWER | 70 | SPARE | 50 | SPARE | 50 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | TOWER LIGHT | 30 | PERIMETER LIGHTS | 30 | ACU 1 | 30 | ACU 2 | 20 | VAN LIGHTS | 20 | C. O. | [12 empty] | Done | OK | [43 empty] | Civil | Others (Flooring) | 1 Lot | [88 empty] | Slight repair on floor
4327 Lila_2_27_17.pdf | 4327 | LILA | 2017-02-27 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed. | OK |  | N/A | CEN Transport, no MW installed | N/A | CEN Transport, no MW installed | OK |  | OK |  | N/A | No 3G is installed. | N/A | CEN Transport, no MW installed | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A | No Bro installed. | N/A | Outdoor cabinet | N/A | CEN Transport, no MW installed | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A | Outdoor site | OK |  | OK |  |  | Off |  | Brgy. Cayupo, Lila, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower / 150 Ft. | Outdoor Site | 24 Hrs. | Caretaker | Yes |  | Diosdado Dahiroc | 9209810288 | 124° 5’ 5” | 09° 35’ 30” | Brgy. Cayupo, Lila, Bohol | 36557 | For Repair | OK | OK | For CSMP Endo | Misaligned gate, for rehab. | Working | OK | Off | OK | OK | OK | OK | Off | None | OK | N/A | OK | Off | N/A | OK | OK | Off | Outdoor site, no equipment shelter. | Off | Off | Off | [6 empty] | Off | Off | Off | [5 empty] | 36526 | Off | Off | Airman | Working | Off | 25 | Working | Off | 5614.6 | None | 90803062017 | Working | None | 210 | 2626040903 | Working | 2 | Working | Outdoor site |  | Off | BTS 3900A | Retrieved |  | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | ATN 950B | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN ATN 950 | 1 |  | 2 | Lila 2G-900 1st E1 | 3 |  | 4 | [31 empty] | Huawei CEN ATN 950 | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | [57 empty] | Huawei (2G) | N/A | N/A | N/A | N/A | 3 | 2 | Shoto | 90 | Shoto | 90 |  |  |  |  | Yes |  | 53.7V | 53.7V |  |  | OK | 25 |  | 15 | CMUA | 15 | BBU 3900 (2G) | 15 |  | 15 | ATN 950B REDUNDANT | 5 |  | 5 |  | 5 |  | 5 | [27 empty] | Huawei (DFON) | 53.3V | 0.0A | 0.5A | 0.5A | 3 | 2 | Shoto | 100 | Shoto | 100 |  |  |  |  | No |  | 53.2V | 53.2V |  |  | Off | 16 | ATN 950B MAIN | 16 |  | 32 |  | 32 |  | 32 |  | 32 |  | 63 |  | 63 | [44 empty] | Off | [5 empty] | Off | [44 empty] | 60 | 5.2 | 20 | Spare | 20 | Perimeter Light | 20 | Tower Light | 63 | BTS 3900A Rectifier (2G) | 70 | Huawei Rectifier (DFON) | [30 empty] | Done | OK | [43 empty] | Civil | Perimeter Gate | 1 Lot | [88 empty] | Misaligned gate for rehab.t
4328 Loboc.pdf | 4328 | Loboc | 2017-02-15 | RSJ | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | DEFECTIVE ATS | OK |  | OK |  | N/A |  | OK |  | OK |  |  | Off |  | Barangay Poblacion, Loboc, Bohol | Residential | Lot | Permanent | Lot | Guyed 150 ft | NA | 24 hrs | Posting Guard | Yes |  | ESTATE OF AGAPITA DANO |  | 124° 2'22.51"E | 9°38'3.32"N | Brgy. Undol, Loboc, Bohol | 3,0 | OK | for CSMP Endo | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | Off | Off | Off |  | Off | Off |  | Off | Off | Off | Outdoor Site | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | 1,0 | None | None | POWERCITY | Defective | None | 45 | Working | CF100 | 2019 | None | 9651460 | None | None |  | 1919020635 | Working |  | Working |  | Huawei BTS3900A | Retrieved | Huawei BTS3900A | Retrieved | Huawei RRU | Retrieved |  | Off |  | Off | Boser | 3 | Retrieved | Off |  | Off |  | Off |  | Off |  | OK | OK | Nokia | Flexihopper | No | 7303000 | 7142000 | -63 | Off | Off | Off | SEVILLA | Huawei | RTN620 | No | 15327 | 14907 | -37.3 | OK | OK | No | LOAY |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI RTN620 | 1 | LOBOC 2G 1ST E1 | 2 | LOBOC 2G 2ND E1 | 3 |  | 4 | SEVILLA 3G 1ST E1 | 5 | SEVILLA 3G 2ND E1 | 6 | SEVILLA 3G 3RD E1 | HUAWEI RTN620 | 7 | SEVILLA 3G 4TH E1 | 8 | SEVILLA 2G 1ST E1 | [8 empty] | FLEXIHOPPER | 7 | SEVILLA 3G 1ST E1 | 8 | SEVILLA 3G 2ND E1 | 9 | SEVILLA 2G 1ST E1 | 11 | SEVILLA 3G 3RD E1 | 12 | SEVILLA 3G 4TH E1 |  |  | HUAWEI RTN620 | 1 | LOBOC 3G | 2 | LOBOC BRO | [68 empty] | HUAWEI |  |  |  |  | 3 | 2 | NARADA | 100 | NARADA | 100 |  |  |  |  | No |  | 49.5 | 49.5 |  |  | OK | 25 | BRO ROUTER | 15 | FAN LOWER | 15 |  | 15 | BATTERY CABINET | 15 |  | 15 | RTN 950 A | 15 | RTN 950 B | 5 |  | 5 | [27 empty] | HUAWEI |  |  |  |  | 2 | 2 | SHOTO | 90 | SHOTO | 90 |  |  |  |  | No |  | 50.5 | 50.5 |  |  | Off | 25 | BRO CMM | 15 | FAN | 15 | RTN 620 | 15 | BBU 3G | 15 | BATTERY CABINET | 5 |  | 5 |  | 5 |  | 5 | [42 empty] | Off | [5 empty] | Off | [44 empty] | 50 | 13.2 | 20 | TOWER LIGHT | 20 | P. LIGHT/C.O. | 20 | BRO CABINET | 63 | 3G CABINET | 70 | 2G CABINET | [30 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | ELECTROMECHANICAL | ATS | 1 | POWERCITY
4331 Sierra Bullones TP.pdf | 4331 | Sierra Bullones TP | 2017-03-16 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK | Defective ATS | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | beside Sierra Bullones Municipal Plaza, Barangay Poblacion, Sierra Bullones, Bohol | Residential | Lot | Permanent | Lot | 150ft SST | Van | 24Hrs | Caretaker | Yes |  | Rogelio Adlaon | 9176879452 | 124.293538° | 9.807579° | Barangay Poblacion, Sierra Bullones, Bohol | 4,0 | OK | For FASG Endo | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2,2 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | 51QSXRACCON19KEDP1C | WCONX019ED1 |  | 51QSXRACCON19KEDT09PC-0529300 | 51QSXRACCON19KED H13PC-0284939 |  | Off | Off | None | 7 | 0.82 |  |  |  | 1,0 | Defective | Defective | KIPOR | Defective | None | 28 | Working | Off | 3959.9 | None |  | Working | Off | 10 inches |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HARRIS |  | Yes | 7149 | 7345 | 0.88804 | OK | OK | Yes | CAMANGAY RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HARRIS | 1 | SIERRA TP 2G 1ST E1 | 2 | SIERRA TP 2G 2ND E1 | [34 empty] | HARRIS | 1 | SIERRA TP 3G | [70 empty] | ELTEK | 54.05 |  | 33 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | A80 |  |  | No |  | 52.5 | 52.4 | 52.3 |  | OK | 100 | BTS3900L LOWER | 100 | BTS3900L UPPER | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | 3G DCCU | 40 | AVIAT B | 40 | AVIAT A | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 16.6 | 70 | ELTEK 1 | 70 |  | 50 | ELTEK 2 | 50 |  | 40 |  | 40 |  | 40 |  | 40 |  | 30 | TOWER LIGHT | 30 | ACU 1 | 30 | PERIMETER LIGHT | 30 | ACU2 | 20 | VAN LIGHT | 20 | C.O. | [12 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | ELECTROMECHANICAL | LIGHTINGS | [5 empty] | ELECTROMECHANICAL | ATS | [5 empty] | CIVIL | SITE PERIMETER
4332 Trinidad_3_02_17.pdf | 4332 | TRINIDAD | 2017-03-02 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK | -35.0 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | OK | See page 5 | OK |  | N/A |  | OK |  | OK | Defective genset cranking module, already requested repair. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Trinidad, Bohol | Residential | Lot | Permanent | Lot | Guyes Tower / 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Victor Dehillo | 9183224638 | 124° 20’ 33.2” | 10° 04’ 28.2” | Brgy. Poblacion, Trinidad, Bohol | 36617 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36617 | OK | Ok | 0 / 1 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDP3C | WCONX019ED1 |  | 51PMXRACCAR19KEDT09PC-0529967 | 51QSXRACCON19KEDT15PC-0722335 |  | Working | Working | Off | 7.8A | 8.1A |  | No brand | No brand | 36526 | Working | Working | Kipor | Working | Off | 30 | Working | Off | 138.8 | Working | 2004-259781 | Working | None | 12 " | 14-1491-0200 | Working | N/A | Working |  | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off | Boser | 3 | Retrieved | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 7866.3 | 8177.62 | -35 | OK | OK | Yes | F74-Talibon |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Talibon | 1 | Trinidad 2G 1st E1 | 2 | Trinidad 2G 2nd E1 | 3 |  | 4 | [31 empty] | facing Talibon | 1 | Trinidad 3G-2100 3G | 2 | Trinidad Bro | 3 |  | 4 | [65 empty] | Emerson | 53.5V | 0.0A | 38.0A | 38.0A | 3 | 3 | Narada | 100 | Narada | 100 | Narada | 100 |  |  | No |  | 53.4V | 53.4V | 53.4V |  | Off | 6 | Smartbro | 6 |  | 6 | DC Fan | 40 | 3G-2100 DCDU 12B | 40 | PLDT | 80 | BTS 3900L Upper | 80 | BTS 3900L Lower | 16 |  | 50 | RTN facing Talibon Main | 50 |  | 50 |  | 50 | RTN facing Talibon Redundant | 50 |  | 50 |  | 6 | [30 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25 | 70 | Emerson | 50 | Spare | 50 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 30 | Spare | 30 | Tower Light | 30 | ACU 2 | 30 | ACU 1 | 20 | Van Outlets | 20 | Van Lights | [14 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 unit | Nokia Empower / SN: 2463112 | WFM, FO | WACU | 1 unit | Carrier, 2HP / SN: 51PMXRACCCAR19KEDC09PC-0140780 | WFM, FO | [32 empty] | Civil | Others (Shelter Flooring) | 1 Lot |  |  |  |  | Civil | Others (Shelter Stairs) | 1 Lot |  |  |  |  | Civil | Others (Tower cable bridge)) | 1 Lot | [74 empty] | Flooring, Shelter Stairs, Cable bridge
4391 Valencia TP (1st Half) 2017v2.pdf | 4391 | Valencia TP Smart | 2017-01-06 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | no microwave radio | N/A |  | OK |  | OK |  | OK |  | N/A | no microwave radio | OK |  | OK | NOC PMR Ctrl# 17Q1-1306 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | defective tower light | Rectification | ceiling needs repair | Rectification | defective perimeter lights | OK |  | AECabral III | B | March 06 2017 | Rizal St. corner Hijalda North Poblacion, Valencia, Negros Oriental | Low land | within premise | Commercial | Standby | GT 150ft | CHB | 24 / 7 | private lot with gate/fence | Yes | 2017 | ANTONIETA DIPUTADO |  | 123.2437 | 9.2841 | Rizal St. corner Hijalda North Poblacion, Valencia, Negros Oriental | defective | OK | OK | OK | For CSMP Endo | for grass cutting | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | defective | OK | Ok | defective | OK | OK | For CSMP Endo | radio ceiling needs repair | WACU | WACU | Off | wconx019ed1 | wconx019ed1 |  | 51qsxraccon19ked b13pc-0061295 | 51qsxraccon19ked t15pc-0755079 |  | Working | Working | None |  |  |  | generic, not used |  | working | Working | None | Powercity | Working | None | 45 | Working | CF100 | working | None | ge2003313139 | Working | None |  |  | Working |  | Defective | on going construction of genset pad and | BTS3900L GSM | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off | Boser | 6 | Off | None |  | Off | BTS3900 LTE | Retrieved |  | Off |  | OK | OK |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | Fiber Switch | No | Trad | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [100 empty] | Eltek | 53.79 | 0 | 38 | 38 | 4 | 3 | Narada | 155 | Narada | 155 | Narada | 155 |  |  | No |  | 53.3 | 53.2 |  |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 |  | 80 | 2G BTS Upper | 80 | 2G BTS Lower | 63 |  | 63 |  | 63 | PLDT Fiber Home | 63 |  | 40 | ECI XDM100 | 40 | 3G | 40 | WBB DCPDB | 40 | LTE TD | 20 | ECI Fiber switch | 20 |  | 20 |  | 20 |  | 10 |  | 10 |  | Eltek | 54.01 | 0 | 8 | 8 | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54 | 53.8 | 53.8 | 53.9 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | PLDT Fiber Home | 63 |  | 63 |  | 63 |  | 63 |  | 40 | ECI Fiber switch | 40 | ECI XDM100 | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | Allied Switch | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 20 | 70 |  | 70 | Eltek Valere 1 | 20 | Cabin CO | 70 | Eltek Valere 2 | 70 | Eltek Valere 2 | 20 | Perimeter / OB lights | 40 | ACU | 40 | ACU | [24 empty] | Done | OK |  | AECabral III | March 06 2017 | Bening rectifier | 1 | decommissioned Bening rectifier w/ modules | WFM | batteries | 12 | defective Narada 155 batteries | WFM | [32 empty] | Electromechanical | perimeter lights | 2 | n.a. | n.a. | n.a. | n.a. | Electromechanical | tower lights | 1 | n.a. | n.a. | n.a. | n.a. | Civil | Equipment shelter | 1 | ceiling | ceiling | n.a. | damaged ceiling
5056-PAMPLONA PLDT-031417.pdf | 5056 | Pamplona PLDT | 2017-03-14 | rdcueco | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | Rectification | rusted tower u bolts | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK | NOC control # 17Q1-1496 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | Rectification |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification |  | Rectification | power cable for rectification | OK |  | Rectification | radio room leaking | OK |  | OK |  |  | A |  | Brgy Nabalabag Pamplona Negros Oriental | Commercial | Lot | Permanent | Lot | 150 ft SST | Van | 24 hrs | Posting Guard | Yes | [7 empty] | OK | OK | OK | OK |  | Defective | OK | OK | For Rehab | OK | OK | OK | For Rehab | OK | OK |  | OK | For Rehab |  | OK | For Rectification | OK |  | WACU | Off | Off | WCARP019EA | 51qsxracc0n19kedB15pc |  | 111604673 | 154316 |  | Working | Working | Off |  |  |  | NA | NA |  | Off | Off | KIPOR | Working | None | 28KVA | Working | CF100 |  | Working | 2006-20688 | Working | None |  |  | Working |  | Working |  | HUAWEI | Off | HUAWEI | Retrieved | HUAWEI | Off | HUAWEI | Off | NA | Off | NA |  | Off | None | HUAWEI | Off | HUAWEI | Off |  | Off |  | OK | OK | HARRIS |  | Yes | 7240 | 7401 | 0.85366 | OK | OK | Yes | V0067 PNOC VALENCIA | HARRIS |  | Yes | 7457 | 7625 | 1 | OK | OK | Yes |  | HARRIS |  | Yes | 7457 | 7625 | 0.85714 | OK | OK | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | ELTEK | 53.98 | 0 | 4 | 4 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN |  | No | [5 empty] | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | HARRIS DCPDB PROTECT | POWERONE | 54.41 | 0 | 22 | 22 | 5 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | Off | [5 empty] | OK | 50 |  | 50 |  | 63 |  | 63 |  | 50 |  | 40 |  | 16 | HARRIS DCPDB MAIN | 16 |  | 16 |  | 10 |  | 10 |  | 10 |  | 10 |  | 6 |  | 6 |  |  |  | 80 | BTS LOWER |  |  | 80 | BTS UPPER | [21 empty] | Off | [5 empty] | Off | [44 empty] | 150 |  | 50 | POWER ONE | 40 | ACU1 | 40 |  | 40 | ACU2 | 40 |  | 40 | ELTEK 2 | 30 | CO | 20 | PERIMETER LIGHT | 70 | ELTEK | 30 | SPARE | [20 empty] | Done | OK
5405 Loon Catagbakan.pdf | 5405 | Loon Catagbakan | 2017-03-08 | RSJ/MRR | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | Bank 1 of Power One Rectifier for replacement | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Sondol, Loon, Bohol | Residential | Lot | Permanent | Lot | SST 150ft | Room | 24hrs | Caretaker | Yes |  | Evelyn Carlon | 9196766378 | 123°47'59.12"E | 9°51'4.02"N | Sandingan Island, Calayugan Norte, Loon, Bohol | 2,2 | OK | For FASG Endo | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED T15PC-0722199 | 51QSXRACCON19KED T15PC-0722205 |  | Working | Working | None | 6 | 7.2 |  |  |  | 1,0 | Defective | Defective | POWERCITY | Working | None | 45 | Working | Off | 576.9 | Off | 1308-0110-0427220 | Working | None | 5.2 inches |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900L | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | AVIAT |  | Yes | 7121; 7747.7 | 7317; 8059.02 | -44.6/-48; -53.8/-59 | OK | OK | Yes | LOON RS | AVIAT |  | Yes | 7177; 7777.35 | 7373; 8088.67 | -34.6/-39.2; -42.1/-47.9 | OK | OK | Yes | TUBIGON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40E | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI CEN | 0/4/0 | LOON CATAGBAKAN 2G 1ST E1 | 0/4/1 | LOON CATAGBAKAN 2G 2ND E1 | [34 empty] | HUAWEI CEN | 0/2/5 | LOON CATAGBAKAN 3G | [18 empty] | AVIAT | DAC GE3 S2P3 | HUAWEI CEN RESILIENCY | [18 empty] | 1 & 2 | HUAWEI CEN 0/6/0 (FACING CALAPE) | 14.23 KM | 7 & 8 | HUAWEI CEN 0/2/0 (FACING LOON RS) | 13.11 KM | [25 empty] | ELTEK | 54.52 |  | 45 |  | 4 | 3 | LYNX | 170 | LYNX | 170 | LYNX | 170 |  |  | No |  | 53.6 | 53.6 | 53.6 |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 | HARRIS B | 63 | BTS3900L UPPER RDNT | 63 |  | 40 | HUAWEI CEN B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 80 | BTS3900L LOWER | POWER ONE | 54.95 |  | 0 |  | 4 | 3 | LYNX | 170 | LYNX | 170 | LYNX | 170 |  |  | Yes |  | 29.8 | 50.1 | 50.1 |  | OK | 50 |  | 50 |  | 63 |  | 63 |  | 40 | HARRIS A | 40 | HUAWEI CEN A | 16 |  | 16 |  | 16 |  | 10 |  | 10 |  | 10 |  | 10 |  | 80 | BTS3900L UPPER | [31 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 25.8 | 70 | POWER ONE | 70 | ELTEK 1 | 20 | PERIMETER LIGHT | 30 | TOWER LIGHT | 30 | ACU 2 | 30 | ACU 1 | 20 | ELTEK 2 | 20 | CO | 30 |  | 20 | VAN LIGHTS | [20 empty] | Done | OK |  |  |  | PANEL ANTENNA | 1 | 1800MHz Panel Antenna |  | ACU | 1 | Condura SN: 048405931 | [33 empty] | CIVIL | PERIMETER GATE ADDITIONAL PADLOCK | 2 |  |  |  |  | CIVIL | PERIMETER WALL FOR REHAB | [5 empty] | ELECTROMECHANICAL | RECTIFIER BATTERY | 1 BANK | LYNX |  | 12V/170AH |  | CIVIL | FUEL TANK | [5 empty] | CIVIL | FUEL LINE
5427 Dumaguete 8 - Banilad (1st Half) 2017v2.pdf | 5427 | Dumaguete 8 - Banilad | 2017-03-02 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 5746-1 (5427 Dum8 facing V0155 Valencia RS) RTN620 ODU1 - EBT07443904 (5427 Dum8 facing 4217 Bacong) HSTX ODU2 - EBT0924E567 (5427 Dum8 facing 4217 Bacong) HSTX | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -31.8 (5427 Dum8 facing V0155 Valencia RS) RTN620 ODU1/2 -42/-37 (5427 Dum8 facing 4217 Bacong) HSTX | OK |  | OK | NOC PMR Ctrl# 17Q1-1207 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Rectification | Control and rectifier module needs replacement in Eltek 2 | OK |  | N/A |  | OK |  | OK |  | OK |  | OK | tower light not working | OK | radio room needs cleaning | OK | needs grass cutting | OK |  | AECabral III | A | March 02 2017 | Purok Kapitan Ano, Brgy. Banilad, Dumaguete City, Negros Oriental | Low land | within premise | Commercial | Stand by | GT 150ft | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | LOURDES PAJULAS,MERCEDES FLORES-PIN |  | 123.2905 | 9.2762 | Purok Kapitan Ano, Brgy. Banilad, Dumaguete City, Negros Oriental | working | OK | OK | OK | For CSMP Endo | needs grass cutting | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | light switch not working | OK | Ok | none | OK | OK | For CSMP Endo | radio room needs cleaning | WACU | WACU | Off | wconx019ed1 | wconx019ed1 |  | 51qsxraccon19ked r14pc-0592265 | 51qsxraccon19ked r14pc-0592314 |  | Working | Working | Off |  |  |  | none |  | working | None | None | Denyo | Working | None | 25kva | Working | CF100 | working | None | 11030401 | Working | None |  |  | Working |  | Working |  |  | Off | BTS3900L GSM | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  |  | Off | None | BTS3900 | Retrieved |  | Off |  | Off |  | OK | OK | Huawei | RTN620 | No | 18985 | 17975 | -31.8 | OK | OK | No | V0155 Valencia RS | Harris | Stratex | Yes | 12905 | 13171 | 1.1351 | OK | OK | No | 4217 Bacong |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | Fiber switch | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Eltek | 53.74 | 1 | 49 | 49 | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 53.4 | 53.5 | 53.5 | 53.6 | OK | 100 | 2G Upper | 100 | 2G Lower | 100 |  | 100 |  | 63 | DCPDB1 | 63 |  | 63 |  | 63 |  | 63 |  | 40 | XDM100 | 40 | 3G | 40 |  | 40 |  | 40 |  | 40 | LTE | 20 |  | 20 |  | 20 |  | 16 |  | 16 | Fiber switch | 16 |  | 16 |  | Eltek | error display | 0 | 0 | 0 | 4 | 3 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 |  |  | No |  | 53.4 | 53.3 | 53.5 |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 | DCPDB1 | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 | XDM100 | 20 |  | 20 |  | 20 |  | 16 | Fiber switch | 16 | Allied switch | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 21 | 70 | Eltek B | 70 | Eltek A | 30 | lights | 30 | Eltek A | 30 | ACU1 | 30 | ACU2 | 20 |  | 20 | C.O. | 20 | T-light / P-light | 20 | C.O. | 70 |  | 70 | Eltek B | [16 empty] | Done | OK |  | AECabral III | March 02 2017 | PowerOne rectifier cabinet | 1 | PowerOne rectifier cabinet | WFM | batteries | 16 | Supersafe 155 | WFM | [32 empty] | ELECTROMECHANICAL | Tower lights | 1 | n.a. | n.a. | n.a. | defective | ELECTROMECHANICAL | Cabin lights switch | 1 | n.a. | n.a. | n.a. | defective | ELECTROMECHANICAL | Rectifier module | 2 | Eltek | Valere |  | defective
5861MT GUIHOB_01052017.pdf | 5861 | Mt. Guihob | 2017-01-05 | rdc/kta | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | 3G RRU no grounding busbar.for rectification of Huawei.3G site not yet accepted | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | 1 pc eltek rectifier module for replacement.already w/ spms request | OK |  | N/A |  | OK |  | OK | no ATS | Off |  | Off |  | Rectification | Van rehab on going | OK |  | OK |  |  | C
732 Bais RS First Half 2017 PMR.pdf | 732 | BAIS RS | 2017-01-12 | KTAmpong | OK |  | N/A |  | Rectification | Uses 38mm sq ground wire instead of 50mm sq as standard. | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | IF cables for clamping | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | Subject for power line rehab - awaiting approval of quotation from WFM | OK |  | OK |  | OK |  | OK |  |  | A
780 Panglao.pdf | 780 | Panglao | 2017-02-23 | RSJ | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Lower Katibo, Brgy. Danao, Panglao, Bohol | Residential | Lot | Permanent | Lot | SST 180ft | Room | 24hrs | Caretaker | Yes |  | SATURNINA E. HORCERADA |  |  |  | LOWER KATIBO PUROK 5 DANAO / PANGLAO BOHOL | 6,2 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 6,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | WACU | FP-51QSXRACCONR19KEDP1C | FP-51QSXRACCONR19KEDP1C | WCONX019ED1 | 51QSXRACCON19KEDR10PC-0505530 | 51QSXRACCON19KEDH10PC-0354593 | 51QSXRACCON19KEDT15PC-0741787 | Working | Working | Working | 7.3 | 6.6 | 7.2 |  |  | 1,0 | None | None | DENYO | Working | Working | 45 | Working | Off | 243.12 | Working | 93546146 | Working | None |  |  | Working |  | Working |  | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | BBU3900+RRU | Retrieved | BBU3900+RRU | Retrieved |  | Off | Boser | 5 | Retrieved | Off | BBU3900+RRU | Retrieved | BBU3900+RRU | Retrieved |  | Off |  | OK | OK | FUJITSU | FRX | Yes | P=6460, CH1=6540, CH2=6620 | P=6800, CH1=6880, CH2=6960 | P=-39/-38, CH1=-37/-40, CH2=-35/-40 | OK | OK | Yes | GORDA RS | FUJITSU | FRX | Yes | P=6500, CH1=6580, CH2=6660,CH3=6500, CH4=6580, CH5=6660 | P=6840, CH1=6920, CH2=7000, CH3=6840, CH4=6920, CH5=7000 | P=-48, CH1=-49, CH2=-55, CH3=-55, CH4=-52, CH5=-54 | OK | OK | Yes | LOON RS | HUAWEI | RTN950 | Yes | 7177 | 7373 | 1.175 | OK | OK | Yes | ENRIQUE VILLANUEVA | AVIAT |  | Yes | L1=8073.845, L2=8192.445 | L1=7762.525, L2=7881.125 | L1=-31/-38, L2=-32/-39 | OK | OK | Yes | PLDT CACERES |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM100 | Yes | Trad | Yes | ECI | XDM 300 | Yes | Trad | Yes | HUAWEI | CEN NE40E | Off | Trad | Yes |  | HUAWEI CEN | 36750 | PANGLAO 2G 1ST E1 | 37115 | PANGLAO 2G 2ND E1 | 36710 | ENRIQUE VILLANUEVA 2G | 41823 | CRUZTELCO JAGNA |  |  |  |  | ECI (FITL) | I1-12 | PLDT ENRISSON LAND | I1-13 | PLDT ENRISSON LAND | [21 empty] | HUAWEI CEN | PP.1 | PANGLAO BRO | PP.2 | PANGLAO BR, JAGNA AND GUINDULMAN BRO | PP.3 | PANGLAO LTE-FDD | PP.4 | ENRISSON LAND I-GATE | PP.5 | PANGLAO ABIS OVER IP | PP.6 | PANGLAO 3G | PP.7 | ENRIQUE VILLANUEVA 3G | PP.8 |  | 36712 | PANGLAO LTE-TDD |  |  | HUAWEI CEN | 38539 | RTN DCN | 38904 | SOUTH CEBU 3G | 39269 | SOUTH CEBU PABIS | [45 empty] | EMERSON | 54.5 |  | 60 |  | 3 | 4 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | No |  | 53.3 | 53.2 | 53.1 | 53.1 | OK | 6 | BATTERY | 6 |  | 80 |  | 80 | BTS3900L LOWER | 50 |  | 100 | DFB B | 50 |  | 50 | SMARTBRO | 50 |  | 50 |  | 50 |  | 40 |  | 6 | [19 empty] | ELTEK | 53.73 | 0 | 83 |  | 3 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.1 | 53.1 | 53 | 52.9 | OK | 100 | DFB A | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 | HUAWEI PDU 1 | 63 | HUAWEI 3G 850 | 40 | XMD100 B | 40 | AVIAT B | 40 | FUJITSU LOON RS B | 40 | FUJITSU GORDA B | 40 | RTN 950 ENRIQUE VILLANUEVA B | 40 | XDM 300 B | 40 | HUAWEI CEN A | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | ELTEK |  |  |  |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 52.5 | 52.4 | 52.3 | 52.2 | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 | FUJITSU LOON RS A | 63 |  | 63 |  | 63 |  | 63 | HUAWEI PDU B | 40 | FUJITSU GORDA A | 40 | XDM 300 A | 40 |  | 40 | RTN950 ENRIQUE VILLANUEVA A | 40 | HUAWEI CEN B | 40 | AVIAT A | 20 |  | 20 |  | 20 |  | 16 | PLDT OSN 500 | 16 |  | 16 |  | 16 |  | 200 | 22.6 | 50 | ELTEK 1A | 50 | ELTEK 2A | 50 | EMERSON | 30 | ACU 1 | 20 | VAN LIGHTS | 20 | C.O. | 30 | TVSS | 20 | ACU DTS | 30 | ACU 2 | 30 | ACU 3 | 30 | ELTEK 1B | 30 | ELTEK 2B | [16 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING
781 Tagbilaran 2.pdf | 781 | Tagbilaran 2 | 2017-02-16 | RSJ | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 0.90682 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | Van Roof for Rehab | OK |  | OK |  |  | A |  | JA Clarin, St., Brgy. Poblacion 3, Tagbilaran City, Bohol | Commercial | Lot | Permanent | Lot | Guyed 150 ft | Room | 24 hrs | Roving Guard | Off |  | CANDIDO KATIPUNAN |  | 123.8586 | 9.6414 | Plaridel St., Sabang, Baliuag | 6,0 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4,0 | OK | Ok |  | OK | OK | OK |  | WACU | WACU | WACU | FP-51PMXRACCARP19KEDP3C | FP-51QSXRACCONR19KEDP1C | WCONX019ED1 | 51PMXRACCAR19KEDT09PC-0537680 | 51QSXRACCONKEDK09PC-0364503 | 51QSXRACCON19KED T15PC-0742275 | Working | Working | Working | 4.7 | 5.7 | 4.6 |  |  | 2,0 | None | None | CUMMINS/DMT | Working | None | 75/180 | Working | CF100 | 4/838.6 | Working | 2008-604235 | Working | None |  |  | Working |  | Working |  | Huawei BTS3900L | Retrieved | Huawei BTS3900L | Retrieved | BBU 3900+RRU | Retrieved | BBU 3900+RRU | Retrieved |  | Off | BOSER | 6 | Retrieved | None | BBU 3900+RRU | Retrieved | BBU 3900+RRU | Retrieved |  | Off |  | OK | OK | Harris Stratex |  | Yes | 13227 | 12961 | 0.89865 | OK | OK | Yes | TAGBILARAN 1 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | BigBox | Yes | Trad | Yes | Huawei | NE 40 | Yes | Trad | Yes | ECI | XDM-100 | Yes | Trad | Yes | [113 empty] | ELTEK | 54.65 | 0 | 82 | 0 | 4 | 4 | LYNX | 170 | LYNX | 170 | LYNX | 170 | LYNX | 170 | No |  | 49.9 | 50 | 50 | 50 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 | BTS3900L UPPER | 80 | BTS3900L LOWER | 80 | DCDU RRU 3G 850 | 80 |  | 63 |  | 63 | LTE TDD | 63 |  | 63 |  | 40 | LTE DCDU | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 20 |  | 10 |  | 10 |  | ELTEK | 54.18 | 0 | 42 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.8 | 53.8 | 53.8 | 53.8 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | HUAWEI CEN BB A | 63 |  | 63 |  | 63 |  | 63 |  | 40 | ECI XDM 100 B | 40 |  | 40 | HUAWEI CEN SB B | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | HARRIS B | 16 |  | 16 |  | 16 |  | POWER ONE | 54.37 | 0.1 | 7.6 | 7.5 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No |  | 53.9 | 53.9 |  |  | OK | 50 |  | 50 |  | 63 | HUAWEI CEN BB B | 16 |  | 16 |  | 40 | HUAWEI CEN SB A | 16 | HARRIS A | 40 | ECI XDM 100 A | 40 |  | 40 | BRO | 40 |  | 40 |  | 16 |  | 6 | LINEDRIVER | 6 |  | 6 | HUAWEI OM500 | 6 | [11 empty] | 100 | 42.4 | 50 | ELTEK 2B | 50 | DMTBATTERY CHARGER | 50 | POWER ONE 1 | 30 | ACU3 | 30 | ACU2 | 30 | ACU1 | 70 | ELTEK1A | 30 |  | 20 | LIGHTINGS | 70 | ELTEK 1B | 30 | POWER ONE 2 | 20 | C.O. |  |  | 70 | ELTEK 2A | [12 empty] | Done | OK | [43 empty] | CIVIL | EQUPMENT SHELTER (ROOF FOR REHAB)
782 BAYAWAN PLDT First Half 2017 PMR v2.pdf | 782 | BAYAWAN PLDT | 2017-03-21 | KTA | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A | PLDT Facility | N/A | PLDT Facility | OK |  | OK |  | Rectification | NEEDS FLOORING REHAB | OK |  | OK |  |  | A |  | VILLAREAL, BAYAWAN CITY, NEGROS ORIENTAL | PLDT COLOC | LOT | PERMANENT | LOT | SST / 42M | VAN | 24 HOURS | GUARD | Yes | [6 empty] | NA | OK | N/A | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED B15PC - 0167153 | 51QSXRACCON19KED T15PC - 0756708 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None |  | Working | None |  | Working | CF200 |  | None |  | Working | None |  |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved |  | Off |  | Off |  | Off | BOSER | 5 | Off | None |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | F30 STA. CATALINA |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK | 53.98 | 1 |  | 16 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 54 | 54.04 | 53.9 | 53.96 | OK | [6 empty] | 100 | BTS 1800 | [18 empty] | 40 | HSTX B | 40 | WBB | [10 empty] | 16 | RTN 950 F F30 STA. CATALINA REDUNDANT |  |  | ELTEK | 53.95 | 0 |  | 13 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.98 | 53.97 | 54.04 | 54 | OK | [6 empty] | 100 | BTS 900 | [20 empty] | 40 | RTN 950 F F30 STA. CATALINA MAIN | [6 empty] | 16 | HSTX MAIN | [21 empty] | No | [5 empty] | Off | [44 empty] | 125 |  | 70 | ELTEK 2 |  |  | 40 | SPARE |  |  | 70 | ELTEK 1 |  |  | 70 | ELTEK 1 |  |  | 30 | ACU 1 |  |  | 30 | ACU 2 |  |  | 20 | C.O. 2 |  |  | 20 | C.O. 1 |  |  | 70 | ELTEK 2 |  |  | 15 | L.O. |  |  | Done | OK
783 PLDT Tanjay First Half 2017 PMR v2.pdf | 783 | PLDT TANJAY | 2017-03-13 | KTA / RDC | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | Rectifier 2 awaiting spare availability for Control Module and 1 pc RM | OK |  | N/A |  | N/A | PLDT Facility | N/A | PLDT Facility | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | BRGY 3., TANJAY CITY, NEGROS ORIENTAL | PLDT COLOC | LOT | PERMANENT | LOT | SST / 42M | VAN | 24 HOURS | GUARD | Yes | [6 empty] | NA | OK | N/A | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | FP-5QSXRACCONR19KEDP1C |  | 51QSXRACCON19KED B15PC - 0154317 | 51QSXRACCON19KED K10PC - 0436389 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None |  | Working | None |  | Working | CF200 |  | Working |  | Working | None |  |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off | BOSER | 5 | Off | None | BBU3900 | Retrieved |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | V4258 SUN DAUIN | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | 5855 ANTULANG | HARRIS | STRATEX | Yes |  |  |  | OK | Off | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK | 54.03 | 1 | 47 | 47 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 54 | 54.04 | 54.01 | 54.02 | OK | 100 | BTS3900L UPPER | 100 | BTS3900L LOWER |  |  |  |  | 63 | LTE FDD | [8 empty] | 40 | WBB | [14 empty] | 20 | DCPDB 1 RGHT SIDE | [8 empty] | ELTEK |  |  |  |  | 3 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.01 | 53.03 | 53.01 | 54.04 | For Rectification | [30 empty] | 20 | DCPDB 1 LEFT SIDE | [27 empty] | No | [5 empty] | Off | [44 empty] | 100 | 100 | 40 | GSM 900 / SPARE |  |  | 40 | ELTEK 2B |  |  | 30 | ELTEK 2 |  |  | 30 | C.O. |  |  | 30 | ACU |  |  | 30 | ACU |  |  | 70 | ELTEK 1A |  |  | 20 | L.O. |  |  | 20 | TOWER LIGHT |  |  | 70 | ELTEK 1 |  |  | Done | OK
794 Tagbilaran 3.pdf | 794 | Tagbilaran 3 | 2017-02-21 | RSJ | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Graham Ave. cor. Ma. Clara St., 2nd District | Commercial | Lot | Permanent | Lot | SST 150 ft | Room | 24hrs | Posting Guard | Yes |  | CASAS DEVELOPMENT CORPORATION |  | 123°51'3.31"E | 9°38'58.52"N | UNIT 507 VENTURE BLDG PRIME & MARKET ST MADRIGAL | 0,2 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 5,1 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | WACU | FP-51QSXRACCONR19KEDP1C | FP-51PMXRACCARP19KEDP3C | WCONX019ED1 | 51QSXRACCON19KEDJ09PC-035020 | 51PMXRACCAR19KEDR07PC-043405 | 51QSXRACCON19KEDM14PC-0516747 | Working | Working | Working | 8 | 7 | 6.8 |  |  | 1,0 | None | None | POWERCITY | Off | None | 75 | Off | CF100 | 727.8 | None | 14962460N[';\ | Working | None |  |  | Working |  | Working |  | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | HUAWEI BBU3900+RRU | Off | HUAWEI BBU 3900+RRU | Off |  | Off | BOSER | 6 | Retrieved | None | HUAWEI BBU3900+RRU | Off | HUAWEI BBU3900+RRU | Off |  | Off |  | Off | Off | Huawei | RTN950 | Yes | 12947 | 13213 | 0.84594 | OK | OK | Yes | Tagbilaran Booy | Huawei | RTN950 | No | 7453.5 | 7614.5 | -34.3 | OK | OK | Yes | Tagbilaran Alturas Mall |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI FAXING BOOY | 1 | BOOY 2G | 2 | PMI 2G | 3 |  | 4 | [5 empty] | HUAWEI FACING ALTURAS | 1 | 3G CLOCKING | [23 empty] | HUAWEI CEN | 1 | PMI AND BOOY 3G | [18 empty] | FACING ALTURAS | 1 |  | 2 |  | 3 | ALTURAS 3G | [45 empty] | ELTEK | 53.97 | 0 | 12 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.1 | 53 | 52.9 | 52.8 | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 | UTAG017/2B | 63 |  | 63 |  | 40 | SMARTBRO | 40 |  | 40 | HUAWEI CEN B | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | HUAWEI RTN FACING BOOY B | 16 |  | 16 | HUAWEI RTN FACING ALTURAS A | 6 | TAG3BTS 2303 002 PS2 CB#2 | ELTEK | 54 | 0 | 52 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 51 | 50.8 | 50.6 | 50.5 | Off | 100 | BTS3900L UPPER | 100 |  | 100 |  | 100 |  | 63 | UTAG017/1B | 63 |  | 63 |  | 63 |  | 63 |  | 40 | LTE DCDU 12-B | 40 | HUAWEI 850 3G | 40 |  | 40 | XMN DC PANEL | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 | HUAWEI RTN FACING ALTURAS B | 16 | HUAWEI RTN FACING BOOY A | POWER ONE | 54.3 |  | 72.3 |  | 5 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | Off |  | 49.9 | 49.9 |  |  | OK | 50 |  | 80 | BTS3900L LOWER | 63 |  | 63 |  | 40 |  | 40 |  | 40 | HUAWEI CEN POWER A | 40 |  | 16 | ROUTER | 63 | UTAG017/1A | 63 | UTAG017/2A | 10 |  | 10 |  | 6 | PLDT OM1000 | 6 | TELINDUS CONCENTRATOR | 6 | TAG3BTS 2303 002 PS1 CB#16 | 63 | 3G/LTE DCDU | [10 empty] | 100 | 34 | 50 | ELTEK 2 | 30 |  | 30 |  | 20 | LIGHTING | 70 | ELTEK 1 | 20 | CO | 30 | ACU 1 | 30 | ACU 2 | 30 | POWERONE B | 20 | ACU 3 | 70 | POWERONE A | 50 | ELTEK3 | [16 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING
795 Jagna_2_22_17.pdf | 795 | JAGNA | 2017-02-22 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK | -33.0 / -39.0 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK | Cruztelco leased E1 | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | OK | Defective ATS, already requested repair | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Birhen sa Barangay, Ilihan Hill, Jagna, Bohol | Residential | Lot | Permanent | Lot | 4L-SST / 150 Ft. | Concrete | 24 Hrs. | Caretaker | Yes |  | ATTY. ALEXANDER VILLACASTIN | 9399167282 | 124° 22’ 25.7” | 09° 39’ 7.4” | Birhen sa Barangay, Ilihan Hill, Jagna, Bohol | 42796 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36678 | OK | Ok | none | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | FP-51PMXRACCARP19KEDP3C |  | 51QSXRACCON19KEDT15PC-0722204 | 51PMXRACCARP19KEDN09PC-0485064 |  | Working | Working | Off | 7.1A | 7.2A |  |  |  | 36526 | None | None | DENYO | Defective | None | 25 | Working | Off | 431 | None | 2363074 | Working | None | 8 inches | 04-0491-0220 | Working | N/A | Working |  | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off | Boser | 6 | Retrieved | None |  | Off |  | Off |  | Off | Normal status | OK | OK | AVIAT | Harris Stratex | Yes | 7295.75 | 7338.25 | 0.84615 | OK | OK | Yes | 3336-Laka RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Laka RS | 1 | Jagna 2G 1st E1 | 2 | Jagna 2G 2nd E1 | 3 |  | 4 |  | 5 |  | 10 | Cruztelco Leased E1 | [26 empty] | facing Laka RS DAC GE | 1 | Jagna 3G-2100 | 2 |  | 3 |  | 4 | [13 empty] | facing Laka RS DAC ES | 1 |  | 2 | Jagna Bro | 3 |  | 4 | [44 empty] | Eltek | 54.04V | 0.0A | 47.0A | 47.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 54.0V | 54.0V | 54.0V |  | Off | 100 | BTS 3900L UPPER | 100 | BTS 3900L LOWER | 100 | WCDMA | 100 |  | 63 | SMARTBRO | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 | CRUZTELCO | 16 | 3336 LAKA RS B | ZTE | 53.6V | 0.0A | 0.6A | 0.6A | 3 | 2 | Narada | 100 | Narada | 100 |  |  |  |  | No |  | 53.8V | 53.8V |  |  | OK | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 40 |  | 40 |  | 40 |  | 40 |  | 16 | 3336 LAKA RS A | 16 |  | 80 |  | 6 |  | 6 | [22 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25 | 50 | ELTEK 2 | 50 | ZTE | 30 | SPARE | 30 | LIGHTINGS | 60 | ELTEK 1 | 30 | C.O. | 30 | ACU 1 | 30 | ACU 2 | 30 | SPARE | 20 | SPARE | 20 | SPARE | [18 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 unit | Nokia Empower / SN: 1011206 | WFM, FO | Rectifier Batteries | 8 pcs. | ACME Narada 155AH, 12V | WFM, FO | WACU | 1 unit | Condura 2HP / SN: 51QSXRACCON19KEDH10PC-0354588 | WFM, FO | [28 empty] | Civil | Others (Genset room ceiling)) | 1 Lot | [88 empty] | Genset room and CR ceiling for rehab
797-DUMAGUETE 4-022317.pdf | 797 | Dumaguete 4 | 2017-02-23 | rdcueco | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | ESN not visible | OK |  | OK |  | OK |  | OK |  | OK | NOC control # 17Q1-1035 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | Larena Drive Taclobo Dumaguete City | Commercial | Lot | Tap to Lessor | Lot | 150 ft SST | Concrete Van | 24 hrs | Roving Guard | Yes |  | Teofilo Bulfa | 9273538938 |  |  |  |  | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | NA | For Rectification | Ok |  | OK | OK | OK |  | WACU | Off | Off | 51qsxracc0n19kedr14pc | 51qsxracc0n19kedn14pc |  | 592306 | 558030 |  | Working | Working | Off |  |  |  | NA | NA |  | Off | Off | DENYO | Working | None | 45KVA | Working | CF200 |  | Working | 2MCNM166677 | Working | None |  |  | Working |  | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | NA | Off | BOSER | 6 | Off | None | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | OK | OK | HARRIS |  | Yes | 7457 | 7625 | 0.88095 | OK | OK | Yes | V0067 PNOC VALENCIA |  |  | Yes |  |  |  | Off | Off | No |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | ECI XDM100 | I5-P9 | WBB | I5-P10 | 3G | I5-P11 | LTE FDD | I5-P12 | PLDT EDC | I5-P13 | ALLIED GIG-E SWITCH NMS | [10 empty] | ECI APOLLO FS | AOC10-P4 | LTE FDD | AOC10-P5 | PNOC VALENCIA 3G | [16 empty] | 42737 | FACING BINAO |  | 15/16 | FACING CALINDAGAN | [26 empty] | ELTEK | 53.85 | 0 | 4 | 4 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No | [5 empty] | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | OLT 2B(FIBERHOME) | 63 |  | 63 |  | 63 |  | 63 | VAPEL(AVIAT MAIN) | 40 | AVIAT DCPDB PROTECT | 40 | ECI XDM100 A | 40 | ECI FS SOURCE A | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | ALLIED TURBO SWITCH | 16 |  | 16 |  | 16 |  | ELTEK | 53.85 | 0 | 16 | 16 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | Off | [5 empty] | Off | 100 | BTS UPPER | 100 |  | 100 |  | 100 |  | 63 | LTE FDD | 63 | OLT 2A(FIBERHOME) | 63 |  | 63 |  | 63 |  | 40 | 3G | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | NOKIA | 54.39 | 0.3 | 33.7 | 33.8 | 6 |  | NARADA | 155 | NARADA | 155 | NARADA | 155 |  |  | Off | [5 empty] | Off | [6 empty] | 50 | VAPEL |  |  |  |  | 50 | ECI XDM100 B | 50 | WBB | 16 | ECI FS SOURCE A | 16 |  | 16 |  | 16 |  | 16 | LTE PWR TDD | 16 |  | 80 | BTS3900L LOWER | [14 empty] | 100 |  | 50 | ELTEK 2A | 50 | NOKIA RECTIFIER | 50 | ELTEK 1A | 30 | ELTEK 1B | 40 | OUTLETS/ACU1 | 40 | ACU2 | 30 |  |  |  | 30 | SPARE | 20 | SPARE | 20 | LIGHTS | 70 | ELTEK 2B | [16 empty] | Off | OK | SHELTER ROOFING AND CEILING FOR RECTIFICATION
798 Dumaguete 5 (1st Half) 2017v2.pdf | 798 | Dumaguete 5 | 2017-03-17 | ASLCal | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | NOC PMR Ctrl# 17Q1-1622 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK | busted light | OK | busted lights | OK |  | AECabral III | A | March 16 2017 | Brgy. Calindagan, Dumaguete South Rd. Dumaguete City, Negros Oriental | Low land | within premise | commercial | Standby | SST 150ft | CHB | 24 / 7 | private lot with gate/fence | Yes | 2017 | ROGELIO MARIANO |  | 123.3006 | 9.2955 | Brgy. Calindagan, Dumaguete South Rd. Dumaguete City, Negros Oriental | some busted | OK | OK | OK | OK | busted lights | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | some busted | OK | Ok | none | OK | OK | OK |  | WACU | WACU | WACU | wconx019ed1 | wconx019ed1 | wconx019ed1 | 51qsxracc0n19ked n14pc-0558021 | 51qsxracc0n19ked r14pc-0592262 | 51qsxracc0n19ked r14pc-0592318 / 0592259 | Working | Working | Working |  |  |  | none |  | working | None | None | Denyo | Working | None | 45 | Working | CF100 | working | None | ge-28085226 | Working | None |  |  | Working |  | Working |  |  | Off | BTS3900L GSM | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | shutdown | Off | Boser | 5 | Retrieved | None | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | OK | OK | Aviat | Stratex | No | 7240 | 7401 | 1.2424 | OK | OK | No | F49 Larena | Aviat | Stratex | No | 7625 | 7457 | 0.84848 | OK | OK | No | 811Dum1 | Aviat | Stratex | No | 7457 | 7625 | 1.0909 | OK | OK | No | 730 Siquijor | Aviat | Stratex | No | 7457 | 7625 | 0.91159 | OK | OK | No | F45 Sibulan | Aviat | Stratex | No | 12905 | 13171 | 0.89362 | OK | OK | No | SPI Ventus |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | Fiber Switch | Yes | Trad | No | ZTE | Small Box CEN | Yes | Trad | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [100 empty] | Eltek | 53.98 | 1 | 42 | 42 | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 54 | 54 | 54 | 54 | OK | 100 | Vapel A2 | 100 |  | 100 |  | 100 |  | 63 | RTN980 facing Sibulan | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 | ETSI (PLDT) | 40 | MSAP Huawei OSN7500 (PLDT) | 40 | DCPDP (PLDT) | 40 | LTE FD | 40 | LTE TD | 20 | Allied Switch | 40 |  | 20 | RTN950 facing Oslob | 16 |  | 16 | Huawei Metro (PLDT) | 16 |  | 16 | ZTE CEN Small Box | Eltek | 54.57 | 0 | 59 | 59 | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 54.5 | 54.5 | 54.5 | 54.5 | OK | 100 |  | 100 |  | 100 |  | 100 | Vapel B2 | 80 | ECI Fiber Switch | 80 |  | 80 |  | 80 |  | 63 | RTN980 Facing Sibulan | 63 |  | 63 |  | 63 |  | 40 | ZTE CEN Small Box | 40 |  | 20 | RTN950 facing Oslob | 40 | ECI XDM300 | 20 | DCPDB-2 Main | 20 | DCPDB-1 Main | 20 |  | 20 | ETSI (PLDT) | 10 | Allied Switch | 10 |  | Nokia EmPower | 52.4 | 0.1 | def | def | 7 | 2 | SacredSun | 600 | SacredSun | 600 |  |  |  |  | No |  | 52.4 | 52.4 |  |  | OK | 80 / 80 | 2G BTS Upper / 2G BTS Lower | 50 | XDM300 / Vapel A 1 | 50 | MSAP Huawei OSN7500 (PLDT) | 50 | WBB (Bro) | 16 |  | 16 |  | 16 | DCPDB-2 Protect | 16 | DCPDB-1 Protect | 63 | ECI Fiber Switch | 63 | Vapel B 1 | 10 | Huawei Metro (PLDT) | [22 empty] | 100 | 25 | 50 | Eltek 1 | 50 | EMPower | 40 |  | 40 | ACU | 30 |  | 30 | ACU | 30 | ACU | 30 | ACU | 20 | Lights | 20 | C.O. | 20 |  | 20 | Optomation |  |  | 60 | Eltek | [12 empty] | Done | OK |  | AECabral III | March 16 2017 | Rectifier Cab | 1 | Decommissioned PSSS Rectifier Cab | WFM | batteries | 24 | defective batts EOS 2V 600Ah | WFM | Transformer | 1 | defective 25Kva transformer | WFM | [28 empty] | Electromechanical | cabin lights | 1 | n.a. | n.a. | n.a. | n.a. | Electromechanical | perimeter lights | 1 | n.a. | n.a. | n.a. | n.a.
799MANJUYOD_01122017.pdf | 799 | Manjuyod | 2017-01-12 | rdc | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Off |  | OK |  | Rectification | Dilapidated ceiling and roof | OK |  | OK |  |  | A
810 DUM2 First Half 2017 PMR v2.pdf | 810 | DUMAGUETE 2 | 2017-01-26 | KTA / RDC | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A | FITL | N/A | FITL | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A | FITL | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | ENDORSED FOR REPLACEMENT OF DCPP and BATTERIES / AWAITING DELIVERY | Rectification | FAST DRAINING BATTERIES / FOR REPLACEMENT | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | ROOFTOP, LEE SUPER PLAZA, DUMAGUETE CITY | MAJOR NODE | ROOFTOP | PERMANENT | INDOOR | SST / 30m | CONCRETE | MALL HOURS | ACCESS PASS | Off |  | DYNAMIC DEVELOPMENT CORP |  |  |  | ROOFTOP, LEE SUPER PLAZA, DUMAGUETE CITY | NA | N/A | N/A | for Replacement | OK | FOR REPLACEMENT OF DOOR KNOB | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | NA | OK | For Rectification | Off |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED R14PC - 0592258 | 51QSXRACCON19KED R14PC - 0592298 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | POWERCITY | Working | None | 60 | Working | CF100 | 25.6 | None | 97 825 568 | Working | None | 500Li |  | Working | 0 | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved | BBU3900 | Retrieved |  | Off | BOSER | 6 | Retrieved | None | BBU3900 | Retrieved | BBU3900 | Retrieved |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | FS | Yes | Trad | Yes | ECI | FS | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | POWER-ONE | 54.38 | 0.2 | 50.2 | 53 | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No |  | 53 | 54.4 |  |  | Off | 50 |  | 50 |  | 63 | VAPEL 01-A | 63 | VAPEL 02-A | 40 | HUAWEI 3G | 40 | HUAWEI 3900 | 16 |  | 40 | LTE DCDU | 40 | HUAWEI BTS3900 |  |  | 80 | BTS3900L |  |  | 40 | WCDMA | 6 |  | 6 | TELLABS B | 6 |  | 6 | [11 empty] | EMPOWER | 53.57 | 0.1 | 42 | 37.4 | 6 | 3 | NARADA | 155 | NARADA | 155 | NARADA | 155 |  |  | No |  | 54.2 | 54 |  |  | Off | 32 |  | 32 |  | 32 | ECI B | 32 | WBB DCPDB | 32 | VAPEL 02-B | 32 |  | 16 | ECI FS SOURCE B | 16 | TELLABS A | 16 |  |  |  | 80 | BTS3900L |  |  | 40 | LTE | [18 empty] | EMPOWER | 54.33 | 0 | 8.2 | 8.2 | 5 | 3 | RITAR | 150 | RITAR | 150 | RITAR | 150 |  |  | No |  | 54 | 54.8 | 54.4 |  | Off | 40 | ECI A |  |  | 40 | VAPEL 01-B | 40 | VAPEL 01-B | [6 empty] | 40 |  | 16 | ECI FS SOURCE A | 16 |  | 80 |  |  |  | 16 |  | 16 |  | 10 |  | 100 |  | 100 | [11 empty] | 250 | 225 | 70 | ACU 1 AND 2 | 50 |  | 70 |  | 50 |  | 20 |  | 50 |  | 70 |  | 50 |  | 20 | CO | 50 |  | 20 |  | 70 | POWER-ONE | 70 |  | 50 |  | 20 | LO | 30 |  |  |  | 50 |  | 80 | ACPDB 2 | 70 | EMPOWER | Done | OK |  |  |  | BATTERY | 12 | HZY12-100FA | WFM | BATTERY | 8 | 12V155FS | WFM | BATTERY | 4 | AG12V155FS | WFM
815 Tagbilaran 1.pdf | 815 | Tagbilaran 1 | 2017-02-22 | RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | BANAT-I HILL, BOOL DISTRICT, TAGBILARAN CITY, BOHOL | RESIDENTIAL | LOT | PERMANENT | LOT | SST 150 FT & SST 180FT | ROOM | 24HRS | POSTING GUARD | Yes |  | TEDDY L. IBAO |  | 123°53'0.86"E | 9°38'7.84"N | 3763 Mabini 4th St., Digos City / Davao Del Sur | 7,0 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 7,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | WACU | WCONX019ED1 | WCONX019ED1 | FP-51PMXRACCARP19KEDP3C | 51QSXRACCON19KED K15PC-0540052 | 51QSXRACCON19KED K15PC-0540056 | 51PMXRACCARP19KED09PC-0461750 | Working | Working | Working | 7.1 | 0.8 | 6.9 |  |  | 2,0 | None | None | POWERCITY | Defective | Off | 75 | Working | Off | 3531.12/325.54 | Working |  | Working | None |  |  | Working |  | Working |  | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900 | Retrieved | HUAWEI BTS3900 | Retrieved |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | FUJITSU | FRX | Yes |  |  | P=-48/-42, W1=-47/-40 | OK | OK | Yes | ARGAO | ERICSSON | MLTN | No | 15215 | 14795 | -37.3 | OK | OK | Yes | SUN DAUIS MAYACABAC | AVIAT |  | Yes | 12961 | 13227 | 0.88428 | OK | OK | Yes | TAGBILARAN 2 | AVIAT |  | Yes | 12933 | 13199 | 0.90369 | OK | OK | Yes | TAGBILARAN AIRPORT | AVIAT |  | Yes | 7625 | 7457 | 1.1709 | OK | OK | Yes | LOAY |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM 300 | Yes | Trad | Yes | ECI | XDM 100 | Yes | Trad | Yes | HUAWEI | CEN BB | Yes | Trad | Yes | [113 empty] | ELTEK | 54.87 | 0 | 48 |  | 4 | 4 | LYNX | 170 | LYNX | 170 | LYNX | 170 | LYNX | 170 | No |  | 52.8 | 52.6 | 52.4 | 52.1 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 | 3G CABINET | 40 |  | 40 | RTN CACERES A | 40 | RTN MANTALONGON A | 20 | RTN UBUJAN A | 16 | RTN CORELLA A | 40 | RTN BALILHAN A | 20 | RTN SUN DAO 2 A | 20 | ERICSSON MLTN DAUIS A | 20 | RTN620 DAO BIT | 16 |  | 16 | CICSO ROUTER 1 | 16 | SSU 1 | 16 |  |  | 54.79 | 0 | 56 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.7 | 53.6 | 53.5 | 53.4 | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 | HSPA RRU | 63 |  | 40 |  | 40 | RTN CACERES B | 40 | RTN MANTALONGON B | 20 | RTN UBUJAN B | 40 | XDM-100 (TAG-3) B | 40 |  | 20 | ERICSSON MLTN DAUIS B | 20 | RTN CORELLA B | 20 | RTN BALILIHAN B | 16 |  | 16 | CISCO ROUTER 2 | 16 | NERA EVO CACERES | 16/80 | RTN SUN DAO 2 B / BTS3900L UPPER | ELTEK | 54.05 | 0 | 53 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.2 | 53.2 | 53.2 | 53.1 | OK | 100 | BSC2408 CAB1 PRI 150A | 100 |  | 100 | NEC DCPDB A | 100 |  | 63 | HUAWEI CEN A | 63 |  | 63 | BSC2408 CAB1 PRI 63A | 63 | BSC2408 CAB0 PRI 63A | 63 |  | 40 | XDM100 (TAG-2) B | 40 | HARRIS DCPDB B | 40 |  | 40 | XDM 300 (TAG-4) A | 40 | XDM 100 (TAG-3) A | 40 |  | 20 |  | 20 | RTN TAGBILARAN POBLACION 2 B | 20 | RTN ARGAO A | 16 |  | 16 | HUAWEI OM1000 | 16 | ANDREW DEHYDRATOR | 16 | SSU B | 200 | 65 | 150 | ACDP MAIN | [6 empty] | 60 | ELTEK 5A | 50 | ELTEK 3B | 70 | ELTEK 5B | 70 | ELTEK 3A | [24 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | ELECTROMEHANICAL | ATS
858-DUMAGUETE 3-020717.pdf | 858 | Dumaguete 3 | 2017-02-07 | rdcueco | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | ESN not visible | OK |  | OK |  | OK |  | OK |  | OK | NOC control # 17Q1-0609 | OK |  | Rectification | Jumper cables for rectification | OK |  | Rectification | canopy surge supressors for regrooming | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | 2 nokia rectifiers for replacement | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Off |  |  | B |  | Hagonoy Drive Brgy. Bunao Dumaguete City |  |  |  |  | GT / 130 ft | Concrete | 24/7 |  | Yes |  | Enrique Larena | [5 empty] | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | NA | For Rectification | Ok |  | OK | OK | OK |  | WACU | Off | Off | 51QSXRACCON19KEDR14PC | 51QSXRACCON19KEDR14PC |  | 592302 | 592304 |  | Working | Working | Off |  |  |  | NA | NA |  | Off | Off | POWERCITY | Working | None | 45KVA | Working | CF100 |  | Working | 11030385 | Working | None |  |  | Working |  | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | NA | Off | BOSER | 6 | Off | None | HUAWEI | Off | HUAWEI | Off |  | Off |  | OK | OK | HARRIS |  | Yes | 8147.97 | 7836.65 | 0.89744 | OK | OK | Yes | V3665 SUN TACLOBO | Alcatel | AWY | No |  |  |  | OK | OK | No | J49 CAMNJAC | HUAWEI | RTN950 | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | ECI XDM100 | I5-P9 | WBB | I5-P10 | 3G | I5-P12 | WIMAX (J49 CAMANJAC) | I5-P13 | LTE FDD | I5-P14 | ALLIED GIG-E SWITCH NMS | I5-P15 | DUM3 HSTX NMS | I5-P17 | HUAWEI RTN NMS FACING J49 CAMANJAC | [6 empty] | ECI APOLLO FS | AOC10-P1 | LTE TDD | AOC10-P2 | SUN 3G | [16 empty] | 42737 | FACING LARENA |  | 15/16 | FACING DARO | 3.1083KMS | [25 empty] | ELTEK | 53.79 | 0 | 71 | 71 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No | [5 empty] | OK | 100 | VAPEL A | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | ECI XDM POWER B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 | ECI APOLLO FS POWER B | 16 | HUAWEI RTN MAIN FC CAMANJAC |  | ALLIED TURBO SWITCH | NOKIA | 54.47 | 0 | 0 | 0 | 7 | [9 empty] | Off | [5 empty] | Off | 60 |  | 40 |  | 40 |  | 10 |  | 40 |  | 16 |  | 16 |  | 16 | HARRIS DCPDB 2 | 40 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 40 | [15 empty] | NOKIA | 0 | 0 | 0 | 0 | 8 | [9 empty] | Off | [5 empty] | Off | 60 | [7 empty] | 50 | VAPEL A |  |  | 50 | ECI XDM100 A | 50 |  | 50 |  | 16 | ECI APOLLO FS A | 16 | HUAWEI RTN FACING J49 B | 16 |  | 16 |  | 16 |  | 80 | BTS3900L LOWER | [56 empty] | Off | Off
F21Alburquerque.pdf | F21 | Alburquerque | 2017-01-23 | RSJ/MRR | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK | -36 | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | 53.3V;12.6A | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A | Outdoor Site | OK |  | OK |  |  | Off |  | Barangay Poblancion, Alburquerque, Bohol | Residential | Lot | Permanent | Lot | Guyed, 150ft | NA | 24hrs | Caretaker | Yes |  | Roman Catholic Diocese of Tagbilaran |  | 123°57'25.20"E | 9°36'44.64"N | Cathedral Church, JS Torralba corner Gallares St., Tagbilaran City | 3,0 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | Off | Off | Off |  | Off | Off |  | Off | Off | Off | Outdoor Site | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | 1,0 | None | None | Powercity | Working | None | 25 | Working | CF100 | 225 | None | 4243368 | None | None |  |  | Working |  | Working |  |  | Off | BTS3900A | Retrieved | RRU | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN 950 | Yes | 7121 | 7317 | -36 | OK | OK | Yes | Tagbilaran Mansasa |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | ATN950b | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei RTN | 1 | Tagbilaran Mansasa 2G 1st E1 | [10 empty] | Huawei CEN | 0/4/1 | Alburquerque 2G 1st E1 | 0/4/2 | Tagbilaran Mansasa 2G 1st E1 | 0/4/3 | Alburquerque 2G 2nd E1 | [40 empty] | Huawei CEN | 0/2/4 | Alburqueque 3G | 0/2/5 | Mansasa 3G | [16 empty] | 0/5/0 | 1&2 | 7.71 Km | 0/6/0 | 7&8 | 13.60 Km | [25 empty] | Huawei |  |  |  |  | 3 | 2 | NARADA | 100 | NARADA | 100 |  |  |  |  | No |  | 53.4 | 53.4 |  |  | OK | 15 | BBU 2G | 15 | FAN | 15 | RTN 950 Main | 5 | RTN 950 Standby | [36 empty] | Huawei | 53.3 | 0 | 12.8 |  | 2 | 2 | SHOTO | 100 | SHOTO | 100 |  |  |  |  | No |  | 53.2 | 53.2 |  |  | OK | 16 | FAN | 16 | ATN950B MAIN | 16 | ATN950B STANDBY | 32 |  | 32 |  | 63 |  | 63 |  | 20 |  | 20 |  | 32 |  | 32 |  | 63 |  | 63 | 3G DCDU | 80 |  | 80 | [30 empty] | Off | [5 empty] | Off | [46 empty] | 20 | Tower Light | 20 | Perimeter Light | 70 | Huawei Rectifier (CEN) | 63 | Huawei Rectifier (2G) | 20 | Huawei Rectifier (3G) | [30 empty] | Done | OK | [129 empty] | 2G and RTN Cabinet wityh Rectifier |  | 3G Cabinet | Huawei CEN Cabinet with Rectifier | Genset
F22 Alicia_3_15_17.pdf | F22 | ALICIA | 2017-03-15 | FHG/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK | Defective ATS, for CSMP visit. Genset is OK. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Alicia, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Danilo Esdrelon | 9298874503 | 124° 26.45' | 09° 53.823' | Brgy. Poblacion, Alicia, Bohol | 42768 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 42768 | OK | Ok | 36526 | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDJ13PC-0317925 | 51QSXRACCON19KEDH13PC-0284944 |  | Working | Working | Off | 6.9A | 7.0A |  |  |  | 36526 | Defective | Defective | Kipor | Defective | None | 28 | Working | Off | 376.7 | None | 2363073 | Defective | None | 400 | 09-0991-0005 | Working | None | None | Exhaust fans were already converted and covered. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Nokia | Flexihopper | No | 7198 | 7359 | -34 | OK | OK | No | 3312-Camangay RS | Huawei | RTN 950 | Off |  |  |  | Off | Off | No | 3312-Camangay RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | Huawei RTN 950 ongoing installation | facing Camangay RS | 1 | Alicia 2G 1st E1 | 2 | Alicia 2G 2nd E1 | 3 | Alicia 3G 1st E1 | 4 | Alicia 3G 2nd E1 | [30 empty] | facing Camangay RS | [7 empty] | 3G Tx via E1 | [63 empty] | 3G Tx is via E1 | Eltek | 54.14V | 0.0A | 35.0A | 35.0A | 4 | 2 | Narada | 155 | Narada | 155 |  |  |  |  | No |  | 54.3V | 54.3V |  |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | BTS 3900L Lower | 63 | BTS 3900L Upper | 63 | 3G-2100 DCDU | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 | RTN facing Camangay RS Main | 20 |  | 20 |  | 16 | FH facing Camangay RS | 16 |  | 16 |  | 16 | RTN facing Camangay RS Rdnt | [15 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 25.3 | 70 | Eltek 1 | 70 | Eltek 2 | 50 | Spare | 50 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 30 | Van Lights | 30 | Van Lights | 30 | Perimeter Lights | 30 | ACU 1 | 20 | Tower Light | 20 | C.O. | [12 empty] | Done | OK | [43 empty] | Civil | Flooring | 1 Lot | [88 empty] | Flooring for repair
F24 Dumaguete 6 (1st Half) 2017v2.pdf | F24 | Dumaguete 6 | 2017-03-09 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK | SN: 9895-1 | OK |  | OK |  | OK |  | OK |  | OK | -30.2 | OK |  | OK | NOC PMR Ctrl# 17Q1-1426 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK | area is low voltage, tap to lessor | OK | ATS not yet terminated to new genset | OK |  | OK | no tower lights | OK |  | OK |  | OK |  | AECabral III | A | March 09 2017 | E. J. Blanco Road, Barangay Piapi, Dumaguete City, Negros Oriental | Low land | within premise | tap to neighbor | Standby | SST 150ft | Collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | SPS. THADEU A. BOLODO & ADELA CLORA |  | 123.305 | 9.3202 | E. J. Blanco Road, Barangay Piapi, Dumaguete City, Negros Oriental | working | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | defective | OK | Ok | defective | OK | OK | For CSMP Endo | cabin floor needs cleaning | WACU | WACU | Off | wconx019ed1 | wconx019ed1 |  | 51qsxraccon19ked n14pc-0567975 | 51qsxraccon19ked r14pc-0592296 |  | Working | Working | None |  |  |  | generic, not used |  | working | Working | None | Perkins Power | Working | None | 25 | Working | CF100 | working | None | ed-11925 | Working | None |  |  | Working |  | Working | defective denyo 25 genset | BTS3900L GSM | Retrieved |  | Off | BTS3900 | Retrieved | BTS3900 | Off |  | Off | Boser | 6 | Retrieved | None | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | OK | OK | Huawei | RTN620 | No | 14739 | 15159 | -30.2 | OK | OK | No | V3664 Silliman Medical |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | Fiber Switch | Yes | Trad | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [100 empty] | Eltek | 54.2 | 1 | 76 | 76 | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 54.2 | 54.2 | 54.2 | 54.2 | OK | 100 | 2G BTS Lower | 100 | 2G BTS Upper | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | LTE TD | 40 | LTE FD | 40 | ECI XDM100 | 40 | WBB Bro | 40 | 3G | 40 |  | 20 |  | 20 |  | 20 |  | 16 | ECI Fiber switch | 16 |  | 16 |  | 16 |  | Eltek | 54.46 | 0 | 5 | 5 | 4 | 3 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 |  |  | No |  | 54.4 | 54.4 | 54.4 |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | XDM100 | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | ECI Fiber switch | 16 | Allied switch | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 22 | 70 | Eltek 2 | 70 |  | 50 | Eltek 1 | 50 | Eltek 2 | 40 |  | 40 |  | 40 |  | 40 |  | 30 | ACU | 30 | C.O. | 30 | ACU | 30 | Perimeter lights | 20 | Cabin lights | 20 | Exhaust fan | 70 | Eltek 1 | [10 empty] | Done | OK |  | AECabral III | March 09 2017 | ACU | 1 | defective WACUs | WFM | batteries | 4 | defective Narada 150 batteries | WFM | batteries | 8 | defective Supersafe batteries | WFM | Siemens SRAL | 1 | decommissioned 2ft antenna w/ ODU | TPE | Rectifier cabinet | 1 | decommissioned Nokia EMPower rectifier cabinet | WFm\ | Rectifier cabinet | 1 | decommissioned PowerOne rectifier cabinet | WFM | [16 empty] | Electromechanical | tower lights | 1 | n.a. | n.a. | n.a. | n.a. | Electromechanical | ATS termination | 1 | kutai | n.a. | n.a. | n.a.
F44 Calape.pdf | F44 | Calape | 2017-03-08 | RSJ/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Desamparados, Calape, Bohol | Residential | Lot | Permanent | Lot | SST 150 ft | Van | 24 hrs | Caretaker | Yes |  | Gertrudes Pernia Real | '411-2214 | 123°52'19.31"E | 9°53'18.90"N | Brgy. Desamparados, Calape, Bohol | 3,0 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 8,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDK12PC-0416768 | 51QSXRACCON19KEDK14PC-0467660 |  | Working | Working | None | 7 | 7 |  |  |  | 1,0 | None | None | DENYO | Working | None | 25 | Working | Off | 173.5 | Working | 347401 | Working | None | 8 inches |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40E | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI CEN | 0/4/0 | CALAPE 2G 1ST E1 | 0/4/1 | CALAPE 2G 2ND E1 | [34 empty] | HUAWEI CEN | 0/2/5 | CALAPE 3G | [39 empty] | 1&2 | 0/2/0 Facing Loon Catagbakan | 14.23Km | 7&8 | 0/6/0 Facing Tubigon | 13.81 Km | [25 empty] | NOKIA EMPOWER | 54.62 |  | 17.2 |  | 3 | 3 | NARADA | 155 | NARADA | 155 | NARADA | 155 |  |  | No |  | 50 | 50 | 50 |  | OK | 40 | HUAWEI CEN B | 40 |  | 40 |  | 40 | DFB B | 40 |  | 40 |  | 16 |  | 16 |  | 16 |  | 6 |  | 6 |  | 6 |  | 80 |  | 6 |  | 100 |  | 100 | [13 empty] | ELTEK | 54.05 |  | 30 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 49.8 | 49.7 | 49.8 |  | OK | 100 |  | 100 |  | 100 | BTS3900L LOWER | 100 | BTS3900L UPPER | 63 |  | 63 |  | 63 |  | 63 | DFB A | 63 | HUAWEI CEN A | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 26.9 | 70 | ELTEK 1 | 70 | NOKIA | 50 | ELTEK 2 | 50 |  | 40 |  | 40 |  | 40 |  | 40 |  | 30 | TVSS | 30 | ACU 1 | 30 | TOWER LIGHT | 30 | ACU 2 | 20 | VAN LIGHT | 20 | CO | [12 empty] | Done | OK | [43 empty] | CIVIL | FLOORING | [5 empty] | CIVIL | FUEL TANK
F45 Sibulan First Half 2017 PMR v2.pdf | F45 | SIBULAN | 2017-01-25 | KTA / RDC | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | POBLACION, SIBULAN, NEGROS ORIENTAL | MAJOR NODE | GREENFIELD | PERMANENT | INDOOR | SST / 42M | CONCRETE | 24/7 |  | Off | [6 empty] | WO | OK | For FASG Endo | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | WO | For Rectification | Ok | NA | OK | OK | OK | FOR RECTIFICATION OF GROUNDING INSTALLATION AT TOWER TOP | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED T15PC - 0756744 | 51QSXRACCON19KED B13PC - 0061293 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | DENYO | Working | None | 45 | Working | CF100 | 424 | None |  | Working | None | 2000 Li |  | Working | 0 | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved | BBU3900 | Retrieved | 3 | retrieved | BOSER | 6 | Retrieved | None |  | Off | BBU3900 | Retrieved |  | Off |  | OK | OK | HARRIS |  | Yes |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | FS | Yes | Trad | Yes | ECI | FS | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK | 2 | 1 | 2 | 2 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 53 | 54.4 |  |  | OK |  |  |  |  | 100 | BTS LOWER | 100 | BTS UPPER | 63 | BRO | 63 | ZTE PROTECTION | 63 | 3G | 63 | WIMAX | 63 | RTN980 SANTANDER PILTEL MAIN | 40 | LTE TDD | [10 empty] | 20 | RTN950 SUN SIBULAN REDUNTANT | 20 | TELLABS B | 20 | TELLABS A | 16 | DCPDB 1 MAIN | 16 | DCPDB 2 MAIN |  |  |  |  | EMPOWER | 53.57 | 0.1 | 32.6 | 32.6 | 4 | 2 | LYNX | 170 | LYNX | 170 |  |  |  |  | No |  | 54.2 | 54 |  |  | Off | [14 empty] | 80 | RTN980 PILTEL SANTANDER | 16 | NOKIA FLEXI | 16 | DCPDB 2 PROTECT | 16 | OPTO | 16 | RTN950 SUN SIBULAN |  |  |  |  | 10 | DCPDB 1 PROTECT | [29 empty] | No | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK | 30 | PL | 70 | EMPOWER | 15 |  | 50 |  | 20 |  | 50 |  | 20 |  | 40 |  |  |  | 40 |  |  |  | 40 |  |  |  | 40 | CO |  |  | 30 |  |  |  | 30 | LO |  |  | Done | OK |  |  |  | RECTIFIER | 1 | NOKIA EMPOWER | WFM | BATTERY | 4 | MARATHON M12V155FT | WFM | BATTERY | 4 | LYNX LNX12G-170FA | WFM
F72 Carmen_3_08_17.pdf | F72 | CARMEN | 2017-03-08 | FHG/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | OK | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | National Hi-way, Poblacion Sur, Carmen, Bohol | Residentail | Lot | Permanent | Lot | 3L-SST and 180 Ft. | Concrete | 24 Hrs. | Caretaker | Yes |  |  |  | 124° 11’ 24” | 09° 49’ 11” |  | 2017-05-08 | OK | for CSMP Endo | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | For Rehab | 2000-06-01 | OK | Ok | None | OK | OK | Off | Cable bridge going to tower for rehab | WACU | WACU | WACU | 51PMXRACCARP19KEDP3C | WCONA019ED | FP-51QSXRACCONR19KEDP1C | 51PMXRACCAR19KEDN07PC-0376536 | 51QSXRACCON19KEDB11PC-0153829 | 51QSXRACCON19KEDK09PC-0364352 | Defective | Working | Working |  | 7.9A | 8.1A |  |  | 2000-01-01 | Off | Off | Denyo | Working | None | 45 | Working | Off | 7906.2 | None | 81789257 | Working | None | 15 inches | 909050145 | Working | N/A | Working | No exhaust fan is installed. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off | 3 | retrieved |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Aviat | Harris Stratex | Yes | 7120.75 | 7177.25 | 0.8747 | OK | OK | Yes | 5841-Sierra RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Sierra RS | 1 | Carmen 2G 1st E1 | 2 | Carmen 2G 2nd E1 | 3 | Carmen 2G 3rd E1 | 4 | [31 empty] | facing Sierra RS (DAC ES) | 1 | Wimax | 2 |  | 3 | Carmen 3G-2100 | 4 | [65 empty] | Nokia | 54.44V | 0.0A | 26.7A | 26.7A | 3 | 2 | Sacred Sun | 300 | Sacred Sun | 300 |  |  |  |  | No |  | 54.5V | 54.5V |  |  | OK | 50 | [5 empty] | 50 | [5 empty] | 50 | Harris A | 10 |  | 16 |  | 16 |  | 16 |  | 63 |  | 40 | ZTE PDU Main |  |  | 80 | BTS 3900L Upper | [14 empty] | ZTE | 53.7V | 0.0A | 27.0A | 27.0A | 3 | 3 | Narada | 100 | Narada | 100 | Narada | 100 |  |  | No |  | 53.8V | 53.8V | 53.8V |  | Off | 100 |  | 100 |  | 63 |  | 63 |  | 63 | 3G BTS 3900 | 63 |  | 50 |  | 50 |  |  |  | 80 | BTS 3900L Lower | 40 |  | 40 |  | 40 | Harris B | 40 | ZTE PDU Redundant | [31 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 19 | 70A | EMPOWER | 50 | ZTE | 20A | C.O. | 20 | LIGHTS | 30A | ACU 1 | 30 | ACU 2 | 30A | SPARE | 30 | ACU 3 | 30 | SPARE | 50 | SPARE | 30 | SPARE | 20 | SPARE | [16 empty] | Done | OK |  |  |  | Transformer | 3 units | Westinghouse 15KVA / 94AM93167, 95AM07893, 95AM92009 | WFM, FO | Transformer | 1 unit | Wagner 15KVA / 1212B1855 | WFM, FO | [32 empty] | Civil | Perimeter Fence | 1 Lot
F73 Inabanga.pdf | F73 | Inabanga | 2017-03-20 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | DEFECTIVE ATS | OK |  | OK |  | OK | DEFEECTIVE EXHAUST FAN | OK |  | OK |  |  | Off |  | Barangay Ilaud, Inabanga, Bohol | RESIDENTIAL | LOT | PERMANENT | LOT | SST 150FT | VAN | 24HRS | CARETAKER | Yes |  | Bernabe Salazar | 9464786357 | 124.065394° | 10.031558° | Barangay Ilaud, Inabanga, Bohol | 1,6 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 7,1 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | WCOX019ED1 |  | 51PMXRACCAR19KEDT07PC-0500622 | 51QSXRACCON19KEDT15PC-0722340 |  | Working | Working | None | 7.75 | 6.3 |  |  |  | 1,0 | Defective | Defective | AIRMAN | Defective | Off | 25 | Working | Off | 1968.3 | Working | 12653365 | Working | None | 13.5 INCHES |  | Working |  | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HARRIS |  | Yes | 7373 | 7177 | 0.084603 | OK | OK | Yes | DAGOHOY | HARRIS |  | Yes | 7345 | 7149 | 0.90024 | OK | OK | Yes | TUBIGON | HUAWEI | RTN950 | No | 7233 | 7429 | -33.8 | OK | OK | Yes | BUENAVISTA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | RTN BUENAVISTA | 1 | BUENAVISTA 2G 1ST E1 | 2 | BUENAVISTA 2G 2ND E1 | 3 | INABANGA LAPCAN SUR 2G | 4 | JETAFE 2G 1ST E1 |  | JETAFE 2G 2ND E1 |  |  | HARRIS CAMANGAY | 1 | INABANGA 2G 1ST E1 | 2 | JETAFE 2G 1ST E1 | 9 | BUENAVISTA 2G 1ST E1 | 16 | INABANGA LAPACAN SUR 2G | 18 | INABANGA 2G 2ND E1 | 19 | BUENAVISTA 2G 2ND E1 | HARRIS CAMANGAY | 20 | JETAFE 2G 2ND E1 | [10 empty] | HARRIS | DAC GE P1 | RTN NMS | DAC GE P2 | 3G CLUSTER | DAC GE P3 | INABANGA 3G |  |  | DAC ES P2 | 3G CLUSTER | DAC ES P3 | JETAFE AND BUENAVISTA 3G | [8 empty] | RTN BUENAVISTA | 1 | BUENAVISTA AND JETAFE 3G | [49 empty] | ELTEK | 54.06 | 0 | 41 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 52.3 | 51.9 | 51.7 |  | OK | 100 | BTS3900L LOWER | 100 | BTS3900L UPPER | 100 | 3G DCDU | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | HARRIS B | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 | RTN BUENAVISTA A | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 |  | ZTE | 53.8 |  | 0 |  | 3 | 4 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | No |  | 52.6 | 52.6 | 52.6 | 52.6 | OK | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 80 |  |  |  | 40 |  | 40 | HARRIS A | 16 |  | 16 |  | 16 |  | 16 | RTN BUENAVISTA B | 6 | FLEXIHOPPER BUENAVISTA | 6 | [20 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 19.6 | 70 | ELTEK 1 | 70 | ZTE | 50 | ELTEK 2 | 50 |  | 40 |  | 40 | TVSS | 40 | ACU 1 | 40 | ACU 2 | 30 | VAN LIGHTS | 30 | C.O. | 30 |  | 30 |  | 20 | PERIMETER LIGHTS | 20 | TOWER LIGHT | [12 empty] | Done | OK |  |  |  | ACU | 1 |  | FO & WFM | RECTIFIER | 1 |  | FO & WFM | [32 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING | [5 empty] | ELECTROMECHANICAL | VAN LIGHTING | [5 empty] | ELECTROMECHANICAL | ATS
F75 Ubay_3_27_17.pdf | F75 | UBAY | 2017-03-27 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | Off |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Barangay Poblacion, Ubay, Bohol | Commercial | Lot | Permanent | Lot | 3L-SST and 150 Ft. | Concrete | 24 Hrs. | Caretaker | Yes |  | Bernardino Teloren | (038) 5188010, 09423163666 | 124° 28’ 15.2” | 10° 03’ 24.9” | Barangay Poblacion, Ubay, Bohol | 36739 | For Repair | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 42918 | OK | Ok | None | OK | OK | OK |  | WACU | WACU | WACU | WCONA019ED | WCONX019ED1 | FP-51QSXRACCONR19KEDP1C | 51QSXRACCON19KEDA12PC-0005984 | 51QSXRACCON19KEDT15PC-0725451 | 51QSXRACCON19KEDB09PC-0093177 | Working | Working | Working | 6.9A | 7.0A | 7.0A |  |  | 36526 | None | None | Denyo | Working | None | 25 | Working | Off | 2778.4 | None | 84-385-296 | Working | None | 12 inches | 12-1291-0405 | Working | N/A | Working | No exhaust fan is installed. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off | Boser | 6 | Retrieved | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | Yes | 8118.32 | 7807 | -33.8 | OK | OK | Yes | F74-Talibon | Huawei | RTN 950 | Yes | 7471 | 7639 | 0.86352 | OK | OK | Yes | V5292-Ubay_Biabas |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Talibon | 1 | Ubay 2G 1st E1 | 2 | Ubay 2G 2nd E1 | 3 | Ubay 2G 3rd E1 | 4 | Ubay_Biabas 2G 1st E1 |  |  |  |  | facing Ubay_Biabas | 1 | Ubay_Biabas 2G 1st E1 | 2 |  | 3 |  | 4 | [18 empty] | facing Talibon | 1 | Ubay 3G-2100 | 2 | Ubay_Biabas 3G-2100 | 3 |  | 4 | Ubay Bro | [12 empty] | facing Ubay_Biabas | 1 | Ubay_Biabas 3G-2100 | 2 |  | 3 |  | 4 | [44 empty] | Eltek | Def. Display | 0.0A | Def. Display | Def. Display | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 52.4V | 52.4V | 52.4V |  | Off | 100 | DFB A | 100 | BTS 3900L Lower | 100 | BTS 3900L Upper | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | Harris DCPDB A | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | RTN facing Ubay_Biabas Rdnt | 16 |  | 16 |  | 16 | RTN facing Talibon Main | Nokia Empower | 54.52V | 0.0A | 21.7A | 21.7A | 4 | 3 | Sacred Sun | 300 | Sacred Sun | 300 |  |  |  |  | No |  | 51.0V | 51.0V |  |  | OK | 40 | DCPDB B | 40 |  | 40 |  | 40 |  | 40 |  | 16 | RTN facing Ubay_Biabas Main | 16 |  | 16 |  | 16 |  | 6 |  | 6 |  | 6 |  | 6 |  | 16 | RTN facing Talibon Rdnt | 16 |  | 100 | DFB B | 100 | [26 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 31.1 | 60 | Eltek 1 | 60 | Empower | 40 | Eltek 2 | 40 | Spare | 30 | C. O. | 30 | ACU 1 | 30 | Spare | 30 | Spare | 30 | ACU 2 | 20 |  | 20 | Lightings | 20 | Spare | [16 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 | Empower / SN: 983435 | WFM, FO | WACU | 1 unit | Condura 2HP / SN: 51QSXRACCON19KEDKO9PC-0393484 | WFM, FO | [32 empty] | Civil | Ceiling (cabin&genset rm) | 1 Lot | [88 empty] | For rehab on the ceiling of cabin and genset room/guard house.
F81 Bayawan TP First Half 2017 PMR v2.pdf | F81 | BAYAWAN | 2017-02-28 | KTA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | ZAMORA ST., BAYAWAN CITY, NEGROS ORIENTAL | RESIDENTIAL | GREENFIELD | PERMANENT | LOT | SST / 42M | VAN | 24 HOURS | CARETAKER | Yes | [6 empty] | WO | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | DEF / 1/1 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED K15PC - 0540072 | 51QSXRACCON19KED B13PC - 0053178 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | POWERCITY | Working | None | 45 | Working | CF100 | 68.9 | None | 800328689 | Working | None | 1000 Li |  | Working | 0 | Working |  |  | Off | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | None | BBU3900 | Retrieved |  | Off |  | Off |  | OK | OK | HARRIS | STRATEX | Yes | 7317 | 7121 | 0.96903 | OK | OK | Yes | J45 MANALONGON | HARRIS | STRATEX | Yes | 7625 | 7457 | 0.86389 | OK | OK | Yes | 5056 PLDT PAMPLONA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | POWER-ONE | 54.36 | 0.1 | 5.4 | 6 | 3 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 53 | 54.4 | 54.35 |  | OK | [16 empty] | 16 | HSTX PROTECT | [26 empty] | ELTEK | 54.93 | 0 | 26 | 26 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 54.2 | 54 | 54.7 | 54.5 | Off |  |  |  |  | 100 | HUAWEI BTS3900L UPPER | 100 | HUAWEI BTS3900L LOWER | 63 | LTE FDD | [10 empty] | 20 | HSTX MAIN | [37 empty] | No | [5 empty] | Off | [44 empty] | 150 | 150 | 50 | TOWER LIGHT | 15 | NO LABEL | 50 | POWER-ONE | 15 | LIGHTS | 40 | NO LABEL |  |  | 40 | PERIMETER LIGHT |  |  | 40 | ACU 2 |  |  | 40 | ACU 1 |  |  | 70 | ELTEK 1 |  |  | 70 | ELTEK 2 |  |  | 20 | EMERGENCY LIGHT |  |  | 20 | CO |  |  | Done | OK
F87 Bilar.pdf | F87 |  | 2017-01-24
GZG TOC Cell Site PMR Checklist and Inventory 3310 Panglao TP SMART.pdf | 3310 |  | 2017-03-03
GZG TOC Cell Site PMR Checklist and Inventory 4207 Tagb Manga.pdf | 4207 |  | 2017-02-07
GZG TOC Cell Site PMR Checklist and Inventory 4282 Dauis SMART.pdf | 4282 |  | 2017-02-14
GZG TOC Cell Site PMR Checklist and Inventory J92 Tagb Wireless.pdf | J92 |  | 2017-02-27
GZG TOC Cell Site PMR Checklist and Inventory V0007 San Isidro.pdf | V0007 |  | 2017-02-13
GZG TOC Cell Site PMR Checklist and Inventory V3683 Tagb Pob2 2-2-2017 Sun.pdf | V3683 |  | 2017-02-07
GZG TOC Cell Site PMR Checklist and Inventory V3684 Tagb Ubujan Sun.pdf | V3684 |  | 2017-02-07
GZG TOC Cell Site PMR Checklist and Inventory V3710 Dauis Sun.pdf | V3710 |  | 2017-02-14
GZG TOC Cell Site PMR Checklist and Inventory V3711 Tagb Cogon 2-8-2017 Sun.pdf | V3711 |  | 2017-02-08
GZG TOC Cell Site PMR Checklist and Inventory V5268 RAMIRO HOSPITAL 2-2-2017 Sun.pdf | V5268 |  | 2017-02-02
GZG TOC Cell Site PMR Checklist Anteequera Jan 17 | V3384 |  | 2017-01-17
GZG TOC Cell Site PMR Checklist Loon TP Jan 26 | 3307 |  | 2017-01-27
GZG TOC Cell Site PMR Checklist V5134Tagb Airport Feb. 8 | V5134 |  | 2017-02-08
J45 MANALONGON First Half 2017 PMR v2.pdf | J45 | MANALONGON | 2017-03-21 | KTA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | CONTROLLER OF ELTEK RECTIFIER NEEDS REPLACEMENT | OK |  | OK |  | N/A | PRIME SITE | Rectification | POWERCITY 45 NEEDS TO BE REPAIRED / 2 PERKINS GENSET FOR INSTALLATION | N/A |  | OK |  | Rectification | NEEDS ROOFING REHAB | OK |  | OK |  |  | C |  | MANALONGON, STA. CATALINA, NEGROS ORIENTAL | RESIDENTIAL | LOT | PRIME GENSET | LOT | SST / 42M | VAN | 24 HOURS | CARETAKER | Yes | [6 empty] | NA | OK | N/A | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | DEF 1/4 | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | FP-51QSXRACCONR19KEDP1C | WCONX019ED1 |  | 51QSXRACCON19KEDT09PC-0529509 | 51QSXRACCON19KEDK15PC-0540029 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | Denyo | Working | None | 20 / 25 | Working | CF200 |  | Working | NA | Working | None | 611 | NA | Working | 0 | Working |  |  | Off | BTS3900L | Retrieved |  | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes |  |  | 0.76562 | OK | OK | Yes | F81 BAYAWAN TP |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK |  |  |  |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 54 | 54.04 | 53.9 | 53.96 | OK | 100 | BTS LOWER | [16 empty] | 40 | HSTX A | [24 empty] | ZTE | 53.4 | 2.5 |  | 14.7 | 2 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 53.5 | 53.6 | 53.2 |  | OK |  |  |  |  | 80 | BTS UPPER | [20 empty] | 40 | HSTX B | [31 empty] | No | [5 empty] | Off | [44 empty] | 150 |  | 100 | SPARE | 70 | ELTEK 2 | 100 | SPARE |  |  | 30 | ACU 2 |  |  | 30 | FAN |  |  | 70 | ZTE RECT |  |  | 30 | C.O. |  |  | 30 | P.L. |  |  | 20 | TOWER LIGHT |  |  | 20 | L.O. |  |  | 70 | ELTEK 1 |  |  | Done | OK
J49 Camanjac (1st Half) 2017v2.pdf | J49 | Camanjac | 2017-03-13 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK | serial nos ODU1 1985-8 ODU2 1988-8 ODU3 1960-8 | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -36.4 ODU2 -35.0 ODU3 -29.4 | OK |  | OK | NOC PMR Ctrl# 17Q1-1477 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK | area is sometimes low voltage, tap to lessor | OK |  | OK |  | OK | defective tower light | OK |  | Rectification | needs grass cutting | OK |  | AECabral III | A | March 13 2017 | Brgy.Camanjac, Dumaguete City, Negros Oriental | Low land | within premise | tap to neighbor | Standby | SST 150ft | CHB | 24 / 7 | private warehouse compound lot with gate/fence | Yes | 2017 | ASR NEGROS ISLE, INC. |  | 123.2755 | 9.3272 | Brgy.Camanjac, Dumaguete City, Negros Oriental | working | For Repair | OK | OK | For CSMP Endo | needs grass cutting | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | none | OK | For Rectification | For CSMP Endo | needs to seal more port holes | WACU | WACU | WACU | wconx019ed1 | fp-51qsxracc0nr19kedp1c |  | 51qsxracc0n19ked t15pc-0756718 | 51qsxracc0n19kedh10pc-035446 |  | Working | Working | None |  |  |  | none |  | working | None | None | PowerCity | Working | None | 45kva | Working | CF100 | working | Working | fd-10043845 | Working | None |  |  | Working |  | Working |  |  | Off | BTS3900L GSM | Retrieved | BTS3900 | Retrieved |  | Off | 3 | retrieved |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN950 | Yes | 15,103/15,047/15,019 | 14,683/14,627/14,599 | -0.035374 | OK | OK | No | 858Dum3 |  |  | No |  |  |  | Off | Off | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [100 empty] | Eltek | 54 | 0 | 38 | 38 | 4 | 4 | Lynx | 170 | Lynx | 170 | Lynx | 170 | Lynx | 170 | Yes | 3 | 53.89 | 53.89 | 53.89 | 53.89 | OK | 16 | RTN 950 | 16 | RTN 950 | 100 |  | 100 |  | 63 | Vapel | 63 |  | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 40 | Vapel | 40 |  | 40 | 3G DCDU | 40 |  | 80 | 2G Lower | 16 | Alcatel DCPDB | 16 | Tellabs | 80 | 2G Upper | [19 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 20 | 50 | Eltek 1 | 50 | Eltek 1 | 40 | ACU 1 | 40 | ACU 2 | 20 | Repeater | 40 |  | 30 | Tower light | 30 | Perimeter lights | 20 | Cabin lights | 20 | Cabin C.O. | [20 empty] | Done | OK |  | AECabral III | March 09 2017 | ACU | 1 | defective WACUs | WFM | [36 empty] | Electromechanical | tower lights | 1 | n.a. | n.a. | n.a. | n.a. | Civil | PERIMETER GATE | 1 | n.a. | n.a. | n.a. | n.a.
V0001 Gorda RS.pdf | V0001 | Gorda RS | 2017-03-01 | RSJ/FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Off |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Mt. Gorda, Sitio Manga, Brgy. Anas, Valencia, Bohol | Government | Lot | Permanent | Lot | SST 150 | Van | 24hrs | Posting Guard | Off |  | DENR-CENRO TAGBILARAN |  | 124°15'11.60"E | 9°36'15.40"N | NEW CAPITOL SITE COGON DISTRICT / TAGBILARAN CITY BOHOL | 6,0 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 8,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | Off | Off | CQXRT195BA | CQXRT195BA |  | 48407343 | 48407335 |  | Working | Working | None | 8.8 | 8.7 |  |  |  |  | None | None | DENYO, POWERCITY | Working | Off | 25, 45 | Working | Off | 4179/191.6 | Off | 90225544 | Working | None | 13 inches |  | Working |  | Working |  |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | FUJITSU | FRX | Yes | 6800/6880/6960 | 6460/6540/6620 | -35/-36,-38/-34, -40/-36 | Off | Off | Off | PANGLAO RS | AVIAT |  | Yes | 7177.25/8236.92/8266.570 | 7373.25/7925.60/7955.25 | -40/-44, -43, -44 | OK | OK | Yes | LAKA RS | AVIAT |  | Yes | 7121 | 7317 | 1.3333 | OK | OK | Yes | VALENCIA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM-100 | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | BENNING | 53.3 |  | 0 |  | 2 | 2 | NARADA | 155 | NARADA | 155 |  |  |  |  | No |  | 52.7 | 52.6 |  |  | Off | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 40 | FUJITSU NFRX FACING PANGLAO B | [28 empty] | ELTEK | 53.83 |  | 1.5 |  | 4 | 3 | NARADA | 155 | NARADA | 155 | NARADA | 155 | NARADA | 155 | No |  | 53.4 | 53.3 | 53.2 | 53.1 | Off | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 |  | 80 |  | 80 |  | 63 | HARRIS LAKA RS A | 63 |  | 63 |  | 63 |  | 40 |  | 40 | RTN PANGLAO A | 40 | BTS3900 2G | 40 | HARRIS VALENCIA A | 20 |  | 20 |  | 20 |  | 20 |  | 10 |  | 10 |  | POWER ONE | 54.4 |  | 25.1 |  | 3 | 2 | POWERSAFE | 155 | POWERSAFE | 155 |  |  |  |  | No | [5 empty] | OK | 50 |  | 50 |  | 63 | FUJITSU NFRX FACING PANGLAO A | 63 | RTN PANGLAO B | 40 | HARRIS LAKA RS B | 40 | AVIAT VALENCIA B | 16 |  | 16 |  | 16 |  | 10 |  | 10 |  | 10 |  | 10 |  | 6 | DC FAN | 6 |  | 6 |  | 6 | HUAWEI RTN FACING LAKA B | [10 empty] | 100 | 29.1 | 70 |  | 70 | POWER ONE | 50 | ELTEK 1 | 50 | ELTEK 2 | 40 |  | 40 | ACU 1 | 40 |  | 40 | ACU 2 | 30 | BENNING | 30 | OUTLET | 30 |  | 30 |  | 20 | LIGHTING | 20 | [13 empty] | Done | OK |  |  |  | Genset | 1 |  | FO and WFM | MW Antenna | 4 | 1pc 8ft., 2pcs. 6ft., 1pc 4ft. | FO and WFM | [32 empty] | CIVIL | GUARD HOUSE
V0008 Sikatuna_3_09_17.pdf | V0008 | SIKATUNA | 2017-03-09 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | N/A | Outdoor site and cabinet | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | Rectification | No ATS is installed. Genset for repair of main alternator, already requested repair. | OK |  | OK |  | N/A | Outdoor site | OK |  | OK |  |  | Off |  | Brgy. Poblacion 1, Sikatuna, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower and 150 Ft. | Outdor site | 24 Hrs. | Caretaker | Yes |  | Fortunato Ahat | 9088888600 | 123° 58’ 11.7” | 09° 41’ 12.4” | Brgy. Poblacion, Sikatuna, Bohol | 2000-03-01 | OK | For FASG Endo | OK | For CSMP Endo | Perimeter fence for rehab, damaged by earthquake. | Working | OK | OK | OK | OK | OK | OK | Off | None | OK |  | OK | Off |  | OK | OK | Off | Outdoor site, no equipment shelter. | Off | Off | Off | [6 empty] | Off | Off | Off | [5 empty] | 0 / 1 | Off | Off | Shinsetsu | None | None | 10 | Working | Off | 53.3 | None | 3160172 | None | None | 24 inches | 2121020085 | For CSMP Endo | None | None | Outdoor site, no WACU and exhaust fan. |  | Off | BTS 3900A | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 8059.02 | 7747.7 | -34 | OK | OK | No | 3386-Corella |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Corella | 1 | Sikatuna 2G-900 1st E1 | 2 |  | 3 |  | 4 | [31 empty] | facing Corella | 1 | Sikatuna 3G-2100 | 2 |  | 3 |  | 4 | [65 empty] | Huawei | N/A | N/A | N/A | N/A | 3 | 2 | Shoto | 90 | Shoto | 90 |  |  |  |  | No |  | 50.1V | 50.1V |  |  | OK | 25 | DCDU | 15 | CMUA | 15 | BBU Power | 15 | FH facing Corella | 15 | RRU 0 | 5 | RRU 1 | 5 | RRU 2 | 5 | RTN facing Corella Main | 5 | MBTS | [41 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 60 | 6.8 | 20 | C.O. | 20 | Perimeter / Tower Light | 60 | BTS 3900A | 63 | Spare | [32 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 unit | APM 200 / SN: 21026200112084E6006A | WFM, FO | [36 empty] | Civil | Perimeter Fence | 1 Lot | [88 empty] | Damaged perimeter barb wire by the earthquake for rehab.
V0067 PNOC Valencia (1st Half) 2017v2-.pdf | V0067 | PNOC Valencia | 2017-01-25 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | ODU1 - EBT1047R212 ODU2 - EBT1047R223 | OK |  | N/A |  | OK |  | OK |  | OK | 0.86933 | OK |  | OK | NOC PMR Ctrl# 17Q1-0324 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK | no ATS | OK |  | OK |  | OK |  | OK |  | OK |  |  | B | Jan 24 2017 | Sitio Ilijan, Brgy. Caidiocan, Valencia, Negros Oriental | High land | center | Tap to neighbor | Stand by | guyed Mono pole 42m | 5ftr collapsible van | daytime only | downhill, muddy | Yes | 2017 | RUFINA M. OJARIO |  | 123.185066° | 9.314216° | Sitio Ilijan, Brgy. Caidiocan, Valencia, Negros Oriental | ok | OK | for CSMP Endo | OK | For CSMP Endo | for grass cutting | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | ok | OK | Ok | none | OK | OK | For CSMP Endo | shelter floor needs cleaning | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | WCONX019ED1 |  | 51PMXRACCAR19KEDN07PC-0376696 | 51QSXRACC0N19KEDT15PC-0756855 |  | Working | Working | Off |  |  |  | NONE |  | WORKING | Off | Off | Cummins Onan | None | None | 40kva | Working | CF100 | working | None | TR1824 | Working | None |  |  | Working |  | None |  |  | Off | BTS3900A | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Aviat | Stratex | Yes | 7625 | 7457 | 0.86933 | OK | OK | Yes | 797 Dumaguete 4 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | 2G | [37 empty] | 1 | PLDT service to PNOC | 2 | 3G | [68 empty] | Huawei | 53.2 |  |  |  | 2 | 2 | Shoto | 90 | Shoto | 90 |  |  |  |  | No | 2 | 52.2 | 52 |  |  | OK | 15 | 2G | 15 | TX DCPDB Left |  |  | 15 | 3G | [6 empty] | 15 | Nokia Packet radio (PLDT) | [28 empty] | Emerson APM200 | 52.5 |  |  |  | 3 | 2 | Sacred Sun | 150 | Sacred Sun | 150 |  |  |  |  | No | 1 | 52.5 | 52 |  |  | OK |  |  | 25 | TX DCPDB Right | [55 empty] | Off | [5 empty] | Off | [44 empty] | 70 | 15 | 50 | WACU | 20 | Tower light | 20 | Cabin lights | 20 | CO | 20 | APM | 20 | Perimeter lights |  |  | 63 | Huawei Rectifier | [24 empty] | Done | OK |  | AECabral III | 42760 | [40 empty] | Electromechanical | perimeter lighting | n.a. | n.a. | n.a. | n.a.
V0938 Guihulngan Malusay (1st Half) 2017v2-.pdf | V0938 | Guihulngan Malusay | 2017-01-24 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | ODU1 - 686-8 ODU2 - 654-8 no ODU grounding | OK |  | N/A |  | OK |  | OK |  | OK | 0.87371 | OK |  | OK | NOC PMR Ctrl# 17Q1-0303 | OK |  | N/A | outdoor site / FTK | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Off | huawei - 0.7A Eltek - 22.0A | Off |  | Rectification | green led indicator "off" | OK |  | N/A |  | OK |  | OK | Grounding cable stolen history | N/A | outdoor site | OK |  | OK |  | AECabral III | B | Jan 24 2017 | Brgy Malusay, Guihulngan, Negros Oriental | Low land | None | Commercial | Inhouse B | SST 150ft | Outdoor FTK w/ roof | 24hrs | Muddy/swampy area | No | 2017 |  |  | 123.274704° | 10.131071° |  | Breaker tripped off upon our arrival | OK | OK | OK | OK | Grounding cable stolen history | Working | OK | OK | For Rehab | OK | For Rehab | For Rectification | Off | OK | OK |  | OK | Ok | none | OK | Off | For CSMP Endo | needs grass cutting | Off | Off | Off | NONE | NONE | NONE |  |  |  | Off | Off | Off | [5 empty] | NONE | Off | Off |  | None | Off |  | None | CF200 | NONE | Defective | 2MGNM312244 | None | None | NONE |  | Off | NONE | None | FTK Outdoor site |  | Off | BTS3900A | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN950 | Yes | 13171 | 12905 | 0.87371 | OK | OK | No | 750 Guihulngan |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | 2G | 2 | 3G 1st E1 | 3 | 3G 2nd E1 | [105 empty] | Eltek | 53.85v | 0A | 26A | 26A | 4 | 4 | Sacred Sun | 150 | Sacred Sun | 150 | Sacred Sun | 150 | Sacred Sun | 150 | No |  | 53v | 53v | 53.4v | 53.4v | OK | 100 | 2G | [10 empty] | 40 | 3G | [6 empty] | 16 | RTN950 TX | [22 empty] | Huawei | 53.5 | 0A | 0.5 | 0.5 | 2 | 2 | Sacred Sun | 180 | Sacred Sun | 180 |  |  |  |  | No |  | 53.2 | 53.5 |  |  | OK | 16 | Cabinet Fan | 16 | RTN650 TX | 16 |  | 16 |  | 32 |  | 63 |  | 63 |  | 20 |  | 20 |  | 32 |  | 32 |  | 63 |  | 63 |  | 80 |  | 80 | [30 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 10 | 50 | Huawei Rectifier | 70 | Eltek 1 | 50 | Eltek 2 | 20 | CO | 20 | TVSS | 20 | Shelter lighting | 20 | Perimeter lights | 20 | Tower lights | [24 empty] | Done | OK | [43 empty] | Electro Mech | Tower Grounding cable | 180ft | n.a. | n.a. | n.a. |  | Electro Mech | TVSS | 1pc | ASCO | 350 series | 1,500V |  | Electro Mech | tower bus bar grounding | 150ft | n.a. | n.a. | n.a. |  | Antenna Sys | ODU grounding | 30mtrs | n.a. | n.a. | n.a.
V0948 Panglao Bellevue.pdf | V0948 | Panglao Bellevue | 2017-02-23 | RSJ | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  |  | Off |  | Doljo Panglao, Bohol | Commercial | Roof Deck | Commercial | Building |  | Van | 8hrs | Admin/Bldg. Security | Off |  | Panglao Bellevue Resort |  | 123°43'52.89"E | 9°35'16.60"N | Doljo Panglao, Bohol | NA | N/A | N/A | OK | OK |  | Off | OK | Off | Off | OK | Off | Off | OK | OK | OK | 4,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONH019ED1 |  | 51QSXRACCON19KED-C12PC-0131171 | 51QSXRACCON19KED-K16PC-1074392 |  | Working | Working | None | 7.6 | 6.8 |  |  |  |  | None | None |  | None | None |  | None | Off |  | Off | 23575422 | Off | None |  |  | Off |  | Off |  | BTS3900 | Retrieved |  | Off | BBU3900 +RRU | Retrieved |  | Off |  | Off |  |  | Off | Off | BBU3900 + RRU | Retrieved |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40E | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | HUAWEI CEN | 1 | PANGLAO BELLEVUE 2G | [36 empty] | HUAWEI CEN | 1 | PANGLAO BELLEVUE 3G |  |  | 3 | PANGLAO BELLEVUE LTE-FDD | [35 empty] | 5&6 | ATN950 0/5/0 |  | 12 | PLDT |  | 23&24 | PLDT |  | 25&26 | ATN950 0/6/0 |  | 47&48 | PLDT | [17 empty] | ELTEK | 54.34 | 0 | 21 |  | 4 | 2 | LYNX | 170 | LYNX | 170 |  |  |  |  | No |  | 50.3 | 50.2 |  |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 | BTS3900 | 80 | DCDU BBU | 80 |  | 80 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 | ATN950 A | 20 | ATN 950 B | 10 |  | 10 | [16 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 12.5 | 70 | ELTEK A | 70 | ELTEK B | 30 | ACU1 | 20 |  | 30 | ACU2 | 20 |  | 20 | LIGHTS | 20 | C.O. | [24 empty] | Done | OK
V0969 Tagbilaran Booy_1_30_17 (2).pdf | V0969 | TAGBILARAN_BOOY | 2017-01-30 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed. | OK |  | OK |  | OK |  | Off |  | OK |  | OK | 3G xml | OK | -31.5/-30.2 dBm fac. Tag 3 -34.4/-35.5 dBm fac. PMI | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A | FTK-Outdoor site | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | Huawei: 53.7V, 53.7V | Rectification | Failed. For replacement | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Booy, Tagbilaran City, Bohol | Residential | Lot | Permanent | Lot | 150 Ft, 3L-SST | FTK-Shelter | 24 Hrs. | Roving Guard | Yes |  | Bellardo Mercader | 9177213683 | 123.8479 | 9.6626 | Brgy. Booy, Tagbilaran City, Bohol | 2000-02-01 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | 2000-01-01 | OK | For Rehab | N/A | OK | OK | For CSMP Endo |  | Off | Off | Off | [6 empty] | Off | Off | Off | [5 empty] | 2000-01-01 | Off | Off | Powercity | Working | Off | 25 | Working | Off | 152.1 | Working | 382962 | None | None | 100 | 20871-00 | Working | 2 | None | Ongoing construction of genset pad and fuel tank pedestal. FTK-Outdoor site, no WACU installed. | BTS 3900 | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | Yes | 13213 | 12947 | 0.86777 | OK | OK | No | 794-Tagbilaran 3 | Huawei | RTN 950 | Yes | 12905 | 13171 | 0.86 | OK | OK | No | V0844-Tagbilaran PMI |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | fac. 794-Tagbilaran 3 | 1 | Tagbilaran Booy 1800 2G 1st E1 | 2 | Tagbilaran PMI 900 2G 1st E1 | [8 empty] | fac. V0844-Tagbilaran PMI | 1 | Tagbilaran PMI 900 2G 1st E1 | [23 empty] | fac. 794-Tagbilaran 3 | 1 |  | 2 |  | 3 |  | 4 | Tagbilaran PMI 3G-2100 | 5 | Tagbilaran Booy 3G-2100 | 6 | [9 empty] | fac. V0844-TagbilaranPMI | 1 |  | 2 |  | 3 | Tagbilaran PMI 3G-2100 | 4 |  | 5 |  | 6 | [40 empty] | Huawei | 53.5V | 0.0A | 34.3A | 34.3A | 2 | 2 | Shoto | 100 | Shoto | 100 |  |  |  |  | No |  | 53.7V | 53.7V |  |  | OK | 16 | Fan | 16 | RTN fac. Tag 3 Standby | 16 | RTN fac. Tag 3 Main | 32 | RTN fac. Tagb-PMI Standby | 32 | RTN fac. Tagb-PMI Main | 63 |  | 63 |  | 20 |  | 20 |  | 32 | BTS 2100 | 32 |  | 63 |  | 63 |  | 80 | BTS 1800 | 80 | [30 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 8.5 | 50 | Rectifier | 50 | Spare | 30 | Spare | 20 | Convenience Outlet | 20 | TVSS | 20 | Tower Light | 20 | Perimeter Light | 20 | Shelter Lighting | [24 empty] | Done | OK |  |  |  | Standby Genset | 1 | Shinsetsu 25 KVA / SN: 1013250331 | WFM, FO | Mobile Genset | 2 | Kipor / No SN | WFM, FO | [122 empty] | No fuel tank delivery
V3308Maribojoc.pdf | V3308 | SUN Maribojoc Poblacion | 2017-01-25 | RSJ/GZG | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK | -36 | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | 53.3V;12.6A | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A | Outdoor Site | OK |  | OK |  |  | Off |  | Barangay Poblacion, Maribojoc, Bohol | Residential | Lot | Permanent | Lot | Guyed, 150ft | Collapsible Van | 24hrs | Caretaker | Yes |  | Roman Catholic Diocese of Tagbilaran |  | 123°50'31.20"E | 9°44'28.32"N | Cathedral Church, JS Torralba corner Gallares St., Tagbilaran City | 3,0 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 1,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C |  | 529987 | 529975 |  | Off | Working | Off | 7.4 | 5.8 |  |  |  | 1,0 | None | None | Shinsetsu | Off | Working | 25 | Off | Off | 310 | Working |  | None | None |  |  | Working |  | None |  | BTS3900 | Retrieved | BTS3900A | Retrieved | RRU | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK |  |  | No |  |  |  | Off | Off | Yes | Tagbilaran Mansasa |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | NE 40 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 0/4/0 | Maribojoc 2G 1st E1 | 0/4/1 | Maribojoc 2G 2nd E1 | [34 empty] | Huawei CEN | 1 | Maribojoc 3G | [39 empty] | 0/6/0 | 1&2 | 15.13 Km | 0/2/0 | 7&8 | 6.73 Km | [25 empty] | Eltek | 53.89 | 3 | 40 |  | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.8 | 53.8 | 53.8 |  | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | Huawei CEN Main | 63 |  | 63 |  | 63 |  | 63 | 3G DCDU | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 80 | BTS3900A 2G | Huawei | 53.5 | 0 | 12.8 |  | 3 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.3 | 53.3 | 53.3 |  | OK | 6 |  | 6 |  | 16 |  | 16 |  | 16 |  | 16 | Huawei CEN Standby | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | BAU | [33 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 18 | 70 | Emerson Rectifier | 32 | ACU 1 | 20 | C.O. | 32 | ACU 2 | 20 | Cabin Light | 70 | Eltek 2 | 20 | Alarmn Box | 20 | P.Light | 70 | Eltek 1 | 20 | OB Light | [20 empty] | Done | Off |  |  |  | Vision Batteries | 8 |  | WFM | [122 empty] | 2G and RTN Cabinet wityh Rectifier |  | 3G Cabinet | Huawei CEN Cabinet with Rectifier | Genset
V3323 San Miguel.pdf | V3323 | San Miguel | 2017-02-17 | RSJ/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy Poblacion. ,San Miguel, Bohol | Residential | Lot | Permanent | Lot | SST 150ft | Van | 24 hrs | Caretaker | Yes |  | NELLY BENDIJO-OLARITA |  | 124°20'18.96"E | 9°59'15.36"N | BRGY. MAHAYAG, SAN MIGUEL | 0,2 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2,0 | OK | Ok | 0 | Off | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C |  | 51PMXRACCAR19KEDT07PC-0479288 | 51PMXRACCAR19KEDH07PC-0198827 |  | Working | Working | None | 5.6 | 8.9 |  |  |  | 1,0 | None | None | POWERCITY | Working | None | 25 | Working | Off | 290.4 | Off | 207NM017340 | None | None |  |  | Working |  | None |  | BTS3900L | Retrieved | BTS3900L | Off | BBU3900 + RRU | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | AVIAT |  | Yes | 7317 | 7121 | 0.90476 | OK | OK | Yes | CAMANGAY RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | AVIAT | 1 | SAN MIGUEL 2G 1ST E1 | 2 | SAN MIGUEL 2G 2ND E1 | [35 empty] | 1 |  | 2 | SAN MIGUEL 3G | [68 empty] | EMERSON | 54 |  | 40 |  | 3 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 |  |  | No |  | 52.3 | 52.1 | 51.8 |  | OK | 6 | BATTERY | 6 |  | 16 |  | 40 | AVIAT CAMANGAY A | 40 | AVIAT CAMANGAY B | 80 | BTS3900A | 16 |  | 50 | DCDU 3G | 50 |  | 50 | 125 | 50 |  | 50 |  | 6 | [34 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 |  | 100 | RECTIFIER | 30 | ACU 1 | 20 | VAN LIGHT | 30 |  | 20 | C.O. | 20 | OB LIGHT | 20 | PERIMETER LIGHT | 30 | ACU 2 | 30 |  | 20 | [21 empty] | Done | OK |  |  |  | BATTERIES | 12 | LYNX 12V 170AH | FO & WFM | [36 empty] | Electromechanical | Perimeter Lighting
V3403 SUN Bien Unido_3_02_17.pdf | V3403 | SUN BIEN UNIDO | 2017-03-02 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK | -40.1 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | OK |  | OK |  | OK | No ATS is installed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Bien Unido, Bohol | Residential | Lot | Permanent | Lot | 4L-SST / 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Herminidla Garcia | 9206009354 | 124° 22’ 36.5” | 10° 08’ 45.4” | Brgy. Poblacion, Bien Unido, Bohol | 42767 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36557 | OK | Ok | None | OK | OK | Off |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDP3C | FP-51PMXRACCAR19KEDP3C |  | 51PMXRACCAR19KEDT09PC-0537679 | 51PMXRACCAR19KEDN09PC-0461752 |  | Working | Working | Off | 8.5A | 7.9A |  |  |  | 36526 | Off | Off | Cumper | None | Defective | 15 | Working | Off | 314.2 | Working | 90803061059 | None | None | 200 | 15-1591-0135 | Working | None | None | No exhaust fan is installed. | BTS 3900A | Retrieved | BTS 3900A | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Ericsson | MLTN 6P | No | 8454 | 8335 | -40.1 | OK | OK | Yes | F74-Talibon |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Talibon | 1 | Bien Unido 3G-2100 1st E1 | 2 | Bien Unido 2G 1st E1 | 3 | Bien Unido 2G 2nd E1 | 4 | Bien Unido 3G-2100 2nd E1 | [30 empty] | facing Talibon |  |  |  | 3G Tx via E1 | [68 empty] | Emerson | 53.5V | 0.0A | 37.0A | 37.0A | 3 | 3 | Narada | 100 | Narada | 100 | Narada | 100 |  |  | No |  | 53.5V | 53.5V | 53.5V |  | OK | 6 |  | 6 |  | 16 |  | 40 | MLTN TRM A | 40 | MLTN TRM B | 50 | 3G-2100 DCDU 12B | 50 |  | 50 |  | 80 | BTS 3900A | 50 |  | 6 | BAU | [37 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 26 | 70 | Rectifier | 32 | ACU 1 | 20 | Lightings | 32 | ACU 2 | 20 | C. O. | 20 | O. B. Light | 20 | Spare | 20 | Perimeter | 20 | Spare | 20 | Spare | [20 empty] | Done | OK | [43 empty] | Civil | Others (Barb wire) | 1 Lot | [85 empty] | BTS 3900A | Transport | Cumper genset | Perimeter barb wire for CSMP rectification
V3419 Baclayon_Sun.pdf | V3419 |  | 2017-01-16
V3424 SUN Dagohoy Poblacion.pdf | V3424 | SUN Dagohoy Poblacion | 2017-02-17 | RSJ/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Off |  | OK | No ATS | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Dagohoy, Bohol | Residential | Lot | Permanent | Lot | SST 150ft | Van | 24 hrs | Caretaker | Yes |  | GERMINIO C. RELAMPAGOS |  | 124°16'22.40"E | 9°53'39.54"N | Brgy. Poblacion, Dagohoy, Bohol | 2,1 | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2,0 | OK | Ok | 0 | OK | OK | OK |  | Off | Off | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C |  | 51PMXRACCAR19KEDN07PC-0376720 | 1PMXRACCAR19KEDN07PC-0376861 |  | Working | Working | None | 7.3 | 7.4 |  |  |  | 1,0 | None | None | TMEE | None | Off | 20 | Working | Off | 75.1 | Working | 100501017020 | None | None |  |  | Working |  | Working |  | BTS3900A | Retrieved |  | Off | BBU3900+RRU | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | No | 14935 | 14515 | -35.4 | OK | OK | Yes | CAMANGAY RS | ERICSSON | MLTN | No | 8335 | 7454 | -36.9 | OK | OK | No | CAMANGAY RS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | ERICSSON MLTN | 1 | SUN DAGOHOY 2G 1ST E1 | 2 | SUN DAGOHOY 3G 1ST E1 | 3 | SUN DAGOHOY 3G 2ND E1 | [105 empty] | EMERSON | 54 |  | 25 |  | 3 | 4 | NARADA | 155 | NARADA | 155 | NARADA | 155 | NARADA | 155 | No |  | 51.8 | 51.6 | 51.5 | 51.4 | OK | 6 | BATTERY | 6 | RTN CAMANGAY B | 16 | ERICOSSON MLTN | 16 | RTN CAMANGAY A | 80 | BTS3900A | 40 | DCDU 3G | 50 |  | 50 |  | 50 |  | 40 |  | 50 |  | 50 |  | 6 | [34 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 21.3 | 70 | RECTIFIER | 30 | ACU 1 | 20 | C.O. | 30 | ACU 2 | 20 | VAN LIGHT | 15 | TOWER LIGHT | 20 | PERIMETER LIGHT | 15 |  | 15 |  | 15 | [21 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | PERIMETER LIGHTING | [5 empty] | CIVIL | SITE PERIMETER
V3425 SUN Lila_Poblacion_2_27_17.pdf | V3425 | SUN LILA_POBLACION | 2017-02-27 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed | OK |  | N/A | CEN Transport, no MW installed. | N/A | CEN Transport, no MW installed. | OK |  | OK |  | OK | 3G xml | N/A | CEN Transport, no MW installed. | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed | N/A | No Bro installed | OK |  | N/A | CEN Transport, no MW installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK | Passed. | OK |  | OK |  | N/A | No genset/ATS installed. | OK |  | OK | CEN Transport, no MW installed. | OK |  | OK |  | OK |  |  | Off |  | Brgy. San Antonio, Lila, Bohol | Residential | Lot | Permanent | Lot | 4L-SST / 150 Ft. | Collapsible | 24 Hrs. | None | Yes |  | Germenia Roble | 9483707223 | 124° 05’ 54.1” | 09° 35’ 25.2” | Brgy. San Antonio, Lila, Bohol | 42768 | For Repair | OK | OK | For CSMP Endo | Gate for repaint | Working | OK | Off | OK | OK | OK | OK | OK | OK | OK | 36617 | OK | Ok | 0 / 1 | OK | OK | For CSMP Endo |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDT07PC3C | WCONX019ED1 |  | 51PMXRACCAR19KEDT07PC-0479318 | 51QSXRACCON19KEDN14PC-0558063 |  | Working | Working | Off | 7.5A | 8.4A |  |  |  | N/A | Off | Off | N/A | None | Working | N/A | Working | Off | N/A | Working | 99652442 | Off | None | N/A | 2626010494 | Off | N/A | Off | No exhaust fan installed. No genset/ATS installed. | BTS 3900A | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK |  |  | No |  |  |  | Off | Off | No |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | ATN 950B | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN ATN 950B | 1 | SUN Lila 2G-1800 1st E1 | 2 |  | 3 |  | 4 |  | 5 |  | 6 | [27 empty] | Huawei CEN ATN 950B | 1 |  | 2 |  | 3 |  | 4 |  | 5 | 0/2/4 SUN Lila 3G-2100 | 6 |  | 7 |  | 8 | [57 empty] | Emerson #1 | 54.0V | 0.0A | 24.0A | 24.0A | 3 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.1V | 54.1V | 54.1V | 54.1V | OK | 6 | BAU | 6 |  | 16 |  | 16 |  | 40 |  | 80 | BTS 3900A | 50 | CEN DCPDB A | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | [19 empty] | Emerson #2 | 54.0V | 0.0A | 1.0A | 1.0A | 3 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.1V | 54.1V | 54.1V | 54.1V | Off | 6 |  | 6 |  | 16 | CEN DCPDB B | 16 |  | 40 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | [34 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 23.2 | 20 | CABIN LIGHT | 70 | EMERSON #1 | 20 | C. O. | 30 | ACU 2 | 30 | ACU 1 | 20 | TOWER LIGHT | 20 | PERIMETER LIGHT | 20 | ALARM | 50 | EMERSON #2 | [22 empty] | Done | OK |  |  |  | WACU | 1 unit | Carrier 2HP / SN: 51PMXRACCAR19KEDT07PC-0479286 | WFM, FO | [36 empty] | Civil | Perimeter Gate | 1 Lot | [87 empty] | No genset/ATS installed | Vehicular gate for repaint
V3426 SUN Loon Cogon Sur_2_8_17.pdf | V3426 | SUN Loon_Cogon Sur | 2017-02-08 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | 3G xml | OK | -42.2 dBm | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek: 54.2V, 54.2V, 54.2V, 54.2V Emerson: 54.5V, 54.5V | OK | Passed. | OK |  | OK |  | Rectification | Genset has defective injection pump. No ATS installed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Cogon Sur, Loon, Bohol | Residential | Lot | Permanent | Lot | Guyed Tower, 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Genara Orcullo-Mejorada | (038) 505 8014 | 123° 47.834' | 09° 47.785' | Brgy. Catagbakan, Loon, Bohol | 2000-04-01 | OK | for CSMP Endo | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2000-02-01 | OK | Ok | 2000-01-01 | OK | OK | Off |  | Off | Off | Off | FP-51PMXRACCAR19KEDP3C | WCONX019KEA |  | 51PMXRACCAR19KEDR07PC-0433391 | 51QSXRACCON19KED19KEAH12PC-0344439 |  | Working | Working | Off | 8.5A | 7.5A |  |  |  | 0/1 | None | None | TMEE | None | Working | 20 | Working | Off |  | Off | 93402873 | None | None | 450 | 707091507 | Off | 0 | Off |  | BTS 3900A | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off | Normal status | OK | OK | Ericsson | MLTN | No | 15327 | 14907 | -42.2 dBm | Off | Off | Off | 3307-Loon TP | Huawei | RTN 950 | No |  |  |  | Off | Off | Yes | 3307-Loon TP |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | Ongoing installation of RTN MW facing Loon TP | Huawei CEN | 1 |  | 2 |  | 3 | SUN Loon Cogon Sur 2G-1800 1st E1 | 4 | [5 empty] | Loon TP | 1 |  | 2 |  | 3 |  | 4 | [18 empty] | Huawei CEN | 1 |  | 2 | SUN Loon Cogon Sur 3G-2100 | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | [5 empty] | Loon TP | [51 empty] | Eltek | 54.07V | 0.0A | 22.2A | 22.2A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.2V | 54.2V | 54.2V | 54.2V | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 | 3G-2100 DCDU | 63 | BTS 3900A | 63 |  | 63 |  | 63 |  | 40 | NE40E-X2-M8 Main | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | RTN facing Loon TP Main | Emerson | 54.5V | 0.0A | 8.0A | 8.0A | 3 | 3 | Narada | 100 | Narada | 100 | Narada | 100 |  |  | No |  | 54.5V | 54.5V | 54.5V |  | OK | 6 | BAU | 6 |  | 16 | MLTN facing Loon TP | 16 | RTN facing Loon TP Rdnt | 40 |  | 40 |  | 50 | NE40E-X2-M8 RDNT | 50 |  | 50 |  | 80 |  | 50 |  | 6 | [36 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 25.1 | 20 | Cabin Light | 30 | Emerson | 20 | C. O. | 30 | ACU 1 | 30 | ACU 2 | 15 | Tower Light | 20 | Perimeter Light | 70 | Eltek 2 | 70 | Eltek 1 | 20 | Spare | [20 empty] | Done | OK | [133 empty] | Ongoing construction of genset pad and fuel tank pedestal
V3428 SUN Tagbilaran Pob. 1_1_31_17.pdf | V3428 | SUN TAGBILARAN POB. 1 | 2017-01-31 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | 3G xml | OK | -46.3/-44.3 dBm fac. Ramiro -40.1/-38.5 dBm fac. Pob. 2 | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | Emerson: 53.6V, 53.6V, 53.6V, 53.6V | OK | Passed. | OK |  | OK |  | N/A | Building site, no ATS/genset installed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Namoc Building, Gallares St., Tagbilaran City, Bohol | Commercial | Roof deck | Permanent | Building | Monopole / 18m | Collapsible | 24 Hrs. | Roving Guard | Yes |  | Avelino Namoc Jr. | (038) 411 3474, 09229564588 | 123.8551 | 9.64 | Namoc Building, Gallares St., Tagbilaran City, Bohol | N/A | N/A | N/A | OK | Off | Building site, roof deck location | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2000-02-01 | OK | Ok | 0/0 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDP3C | FP-51PMXRACCAR19KEDP3C |  | 51PMXRACCAR19KEDT09PC-0537666 | 51PMXRACCAR19KEDT09PC-0537665 |  | Working | Working | Off | 7.7A | 7.9A |  |  |  | N/A | None | None | N/A | None | Working | N/A | Working | Off | N/A | Working | 10155552 | None | None | N/A | 19271-00 | Off | N/A | Off | Building site, no genset/ATS installed. | BTS 3900A | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 620 | No | 19480 | 18470 | 0.97743 | OK | OK | No | V5268-SUN Tagbilaran Ramiro Hospital | Huawei | RTN 620 | No | 18360 | 19370 | 1.0416 | OK | OK | No | V3683-SUN Tagbilaran Pob. 2 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing SUN Tagb. Ramiro Hosp. | 1 |  | 2 |  | 3 | Ramiro Hosp 2G-1800 1st E1 | [6 empty] | facing SUN Tagb. Pob. 2 | 1 |  | 2 | Tagb Pob 1 2G-1800 1st E1 | 3 |  | 4 |  | 5 | Ramiro Hosp 2G-1800 1st E1 | 6 | [14 empty] | SUN Tagb Ramiro Hospital | 1 | Ramiro Hospital 3G-2100 | [18 empty] | SUN Tagb Pob 1 | 1 | Tagb Pob 1 3G-2100 | 2 | Ramiro Hospital 3G-2100 | [47 empty] | Emerson | 53.5V | 0.0A | 35.0A | 35.0A | 3 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.6V | 53.6V | 53.6V | 53.6V | OK | 6 |  | 6 |  | 6 |  | 16 |  | 80 | BTS 3900A | 50 | RTN DCPDB | 50 |  | 50 |  | 50 |  | 50 | NODE B DCPDB | 80 |  | 6 | BAU | [35 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 25 | 70 | Rectifier | 32 |  | 20 | C. O. | 32 | ACU 2 | 20 | Cabin Light | 20 | Tower Light | 20 | Spare | 20 | ACU 1 | 20 | Spare | 20 | Spare | [20 empty] | Done | OK |  |  |  | Rectifier Batteries | 8 | ACME Narada Batteries, 100Ah, 12V | WFM, FO | [126 empty] | No ATS, genset installed on site.
V3430 SUN Tubigon Cabulihan.pdf | V3430 | SUN Tubigon Cabulihan | 2017-03-14 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  |  | Off |  | Brgy. Macaas, Tubigon, Bohol | Residential | Lot | Permanent | Lot | Guyed 150 ft | NA | 24hrs | N/A | Off |  | LUCIO A. REBUCAS |  | 123.985526° | 9.948631° | Brgy. Macaas, Tubigon, Bohol | 3,0 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | NONE | None | None |  | None | None |  | Working | Off |  | Working | 93825768 | None | None |  |  | Off |  | None |  | BTS3900A | Retrieved |  | Off | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | ERICSSON | MLTN | No | 8426 | 8307 | -41.3 | OK | OK | No | TUBIGON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | SUN TUBIGON CABULIHAN 3G 1ST E1 | 2 | SUN TUBIGON CABULIHAN 2G | 3 | SUN TUBIGON CABULIHAN 3G 2ND E1 | [105 empty] | ELTEK | 53.97 | 0 | 24 |  | 4 | 4 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | No |  | 51.9 | 51.9 | 52.1 | 52.1 | Off | 100 | DCDU 2G | 100 | DCDU 3G | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 16 |  | 16 |  | 16 | [34 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 60 | 20.2 | 50 | BTS3900A | 20 | TOWER LIGHT | 20 |  | 20 | PERIMETER LIGHT | 70 | ELTEK | 20 | [29 empty] | Done | OK |  |  |  | BATTERIES | 8 | NARADA 12V 100AH | FO & WFM
V3431 SUN Ubay_Fatima_3_27_17.pdf | V3431 | SUN UBAY_FATIMA | 2017-03-27 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | OK |  | OK |  | OK | Defective ATS, already requested repair/replacement. Genset is OK on manual mode. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Barangay Fatima, Ubay, Bohol | Commercial | Lot | Permanent | Lot | 4L-SST and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Euteqio Bernales |  | 124° 28’ 35.2” | 10° 03’ 19.4” | Barangay Poblacion, Ubay, Bohol | 36617 | OK | for CSMP Endo | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 42826 | OK | Ok | 0 / 1 | OK | OK | OK |  | WACU | WACU | WACU | FP-51PMXRACCAR19KEDP3C | FP-51PMXRACCAR19KEDP3C |  | 51PMXRACCAR19KEDT07PC-0480122 | 51PMXRACCAR19KEDT07PC-0479293 |  | Working | Working | Off | 6.9A | 7.2A |  |  |  | 36526 | None | None | TMEE | Defective | None | 20 | Working | Off | 65.3 | Working | 2006-270677 | Defective | None | 10.5 inches | 12-1291-0409 | Working | None | Working | No exhaust fan is installed. | BTS 3900A | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | Yes | 8059 | 7747.7 | 0.95767 | OK | OK | No | F74-Talibon |  |  | Off |  |  |  | Off | Off | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Talibon | 1 | Ubay_Fatima 2G 1st E1 | 2 |  | 3 |  | 4 | [6 empty] | 1 |  | 2 |  | 3 |  | 4 | [18 empty] | facing Talibon | 1 | Ubay_Fatima 3G-2100 | 2 |  | 3 |  | 4 | [14 empty] | 1 |  | 2 |  | 3 |  | 4 | [44 empty] | Emerson | 54.1V | 0.0A | 28.0A | 28.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.5V | 53.5V | 53.5V |  | OK | 6 | BAU | 16 |  | 16 |  | 6 |  | 6 |  | 40 |  | 80 | BTS 3900A | 50 |  | 50 |  | 50 |  | 50 |  | 50 | RTN facing Talibon Main | 50 | RTN facing Talibon Redundant | 40 | 3G-2100 DCDU | [31 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 17 | 20 | Lightings | 100 | Emerson Rectifier | 20 | C. O. | 30 | ACU 1 | 30 | ACU 2 | 20 | Alarm | 20 | Tower Light | 20 | Perimeter Lights | 20 | Spare | 20 | Spare | [20 empty] | Done | OK |  |  |  | MW Antennas | 2 units | 1.2 MW antenna / Ericsson | FO |  | 2 units | 1.8 MW antenna / Ericsson | FO | [32 empty] | Civil | Perimeter Fence | 1 Lot | [88 empty] | Barb wire pole for repair.
V3665 SUN Dumaguete City Poblacion No 4 1 - Taclobo (1st Half) 2017v2.pdf | V3665 | SUN Dumaguete City Poblacion No 4 1 - Taclobo | 2017-02-09 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 5870-1 (V3665 Taclobo facing V3745 Silliman Heights) RTN620 ODU1 - 4831-1 (V3665 Taclobo facing V3750 Calapan) RTN620 ODU1 - 6330-1 (V3665 Taclobo facing V3747 Motong) RTN620 ODU1 - 3566-1 (V3665 Taclobo facing V3748 Mangnao) RTN620 ODU1 - a231028fcj (V3665 Taclobo facing V3744 Brgy3) Minilink TN ODU1 - a23109v6vy (V3665 Taclobo facing V3697 Sibulan) Minilink TN ODU2 - a23109v44a (V3665 Taclobo facing V3697 Sibulan) Minilink TN | OK |  | N/A |  | OK |  | OK |  | Rectification | ODU1 -38.4 (V3665 Taclobo facing V3745 Silliman Heights) RTN620 ODU1 -46.3 (V3665 Taclobo facing V3750 Calapan) RTN620 , for fine tuning ODU1 -36.3 (V3665 Taclobo facing V3747 Motong) RTN620 ODU1 -35.6 (V3665 Taclobo facing V3748 Mangnao) RTN620 ODU1 -20.0 (V3665 Taclobo facing V3744 Brgy3) Minilink TN ODU1 -41.6 (V3665 Taclobo facing V3697 Sibulan) Minilink TN ODU2 -46.0 (V3665 Taclobo facing V3697 Sibulan) Minilink TN | OK |  | OK | NOC PMR Ctrl# 17Q1-0801 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | genset not in auto mode | OK |  | OK |  | OK |  | Rectification | defective photocell | OK |  | AECabral III | B | Feb 14 2017 | Ceres Bus Liber Lot, Brgy Bagacay, Dumaguete City, Negros Oriental | Low land | within premise | Commercial | Standby | SST 150ft | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | Ceres Bus Liner |  | 123.2942 | 9.3037 |  | def photocell | OK | OK | OK | For CSMP Endo | for grass cutting | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | def, busted lights | OK | Ok | not working | OK | OK | For CSMP Endo | for cleaning | WACU | WACU | Off | wconx019ed1 | wconx019ed1 |  | 51qsxraccon19ked r14pc-0592308 | 51qsxraccon19ked r14pc-0592331 |  | Working | Working | Off |  |  |  | Telecool FC-S |  | WORKING but not in auto | Working | None | WEICHAI | Working | Working | 25 KVA | Working | CF100 | working | Working | 2004-248220 | Working | None |  |  | For CSMP Endo |  | Working | Genset not in auto | BTS3012 | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | For Rectification |  | Off |  | Off |  | Off | 3G with clocking alarm | OK | OK | Huawei | RTN620 | No | 18765 | 17755 | -46.3 | OK | OK | No | V3750 Calapan | Huawei | RTN620 | No | 19645 | 18635 | -35.6 | OK | OK | No | V3748 Mangnao | Huawei | RTN620 | No | 15243 | 14823 | -38.4 | OK | OK | No | V3745 SIlliman Heights | Huawei | RTN620 | No | 15327 | 14907 | -36.3 | OK | OK | No | V3747 Motong | Ericsson | Minilink TN | No | 15187 | 14767 | -20 | OK | OK | No | V3744 Brgy3 |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Aviat facing Mt Guihob | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Emerson | 54.3 | 0 | 51 | 51 | 5 | 2 | SacredSun | 180 | SacredSun | 180 |  |  |  |  | No |  | 54.2 | 53.8 |  |  | OK | 16 | Minilink E | 16 | Minilink E | 40 | RTN DCPDB1 | 16 | Minilink TN | 40 | RTN DCPDB2 | 10 | Heat Extractor | 10 | Heat Extractor contorl unit | 40 |  | 40 |  | 40 |  | 40 |  | 50 |  | 50 |  | 50 | 2G | 10 | Allied Switch | 25 | DCPDB1 | 25 | DCPDB1 | 50 | 3G | [23 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 15 | 20 | Lighting | 60 | Emerson Rectifier | 20 | CO | 60 | Emerson Rectifier | 30 | ACU1 | 30 | ACU2 | 20 | OB Light | 20 | Perimeter light | 30 |  | 30 |  | 20 |  | 20 | [17 empty] | Done | OK |  | AECabral III | 42765 | Access cab | 1 | BTS 3012 | Build | [36 empty] | ELECTROMECHANICAL | Perimeter lightings | 1 | n.a. | n.a. | 10watts | needs photocell
V3666 Sun Hilaitan Guihulngan (1st Half) 2017v2.pdf | V3666 | Sun Hilaitan Guihulngan | 2017-03-14 | ASLCal | Rectification | with sec3 VSWR alarm, but no antenna system error with site master | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | ODU1 - -43.1 Ericsson TN | OK |  | N/A |  | OK |  | OK |  | OK | -43.1 Ericsson TN facing Hilaitan Smart | OK |  | OK | NOC PMR Ctrl# 17Q1-1497 | OK |  | N/A | outdoor site | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | huawei - 22.0A | OK |  | Rectification |  | OK |  | N/A |  | OK |  | OK |  | N/A | outdoor site | OK |  | OK |  | AECabral | A | March 14 2017 | Barangay Hilaitan, Guihulngan, Negros Oriental | low land | None, outdoor | Commercial | Inhouse B | SST 150ft | none | 24hrs | with gate/fence, no caretaker | Yes | 2017 | HILARION B. MACALUA JR. |  | 123.3196 | 10.2453 |  | with one busted bulb | For Repair | OK | OK | For CSMP Endo | for grass cutting, gate repair | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | none | OK | Ok | none | OK | OK | OK | outdoor site | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | None | Off | Off |  | None | None |  | Working | CF100 |  | Defective | 209nm099065 | None | None |  |  | Off |  | None | outdoor site | BTS3012 | Retrieved |  | Off |  | Off |  | Off |  | Off |  |  | Off | For Rectification |  | Off |  | Off |  | Off | sec3 VSWR alarm | OK | OK | Ericsson TN | TN | No | 8426 | 8307 | -43.1 | OK | OK | No | V5248 Hilaitan Smart |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | Hilaitan Sun 2G DCS | [109 empty] | Eltek Outdoor | 54.2 | 0 | 22 | 22 | 4 | 4 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 | No |  | 54.2 | 54.2 | 54.2 | 54.2 | OK | 100 |  | 100 | BTS 3012 | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 16 |  | 16 |  | 16 | [34 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 60 | 15 | 50 |  | 40 | BTS 3012 | 20 | CO | 70 | Eltek Outdoor | 20 | OB Lights | 20 | Perimeter lights | [28 empty] | Done | OK |  | Antonio E. Cabral III | March 14 2017 | Ericsson Outdoor cab | 1 | Ericsson Outdoor cab | WFM | [36 empty] | Civil | Perimeter gate | 1 | n.a. | n.a. | n.a. | n.a. | Electro Mech | Perimeter light | 1 | n.a. | n.a. | n.a. | n.a.
V3669 SUN Valencia (Luzurriaga) Bajumpandan (1st Half) 2017v2.pdf | V3669 | SUN Valencia TP | 2017-03-07 | ASLCal | OK |  | N/A |  | Rectification | heliax cables not grounded at bottom part of tower | N/A |  | N/A |  | N/A |  | OK |  | OK | on going installation of RTN950 facing V3665 Taclobo | OK |  | N/A |  | OK |  | OK |  | OK | 0.90278 | OK |  | OK | NOC PMR Ctrl# 17Q1-1338 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Rectification | Defective AC breaker to outdoor BTS | Rectification | ATS not yet install, genset defective cranking module | OK |  | Rectification | grounded tower lights when raining | OK |  | Rectification | defective perimeter lights | OK |  | AECabral III | B | March 07 2017 | Paterna Init, Burgos St., Valencia Negros Oriental | Low land | within premise | Commercial | Standby | GT 150ft | Collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | ERMA T. INIT |  | 123.2443 | 9.2772 | Paterna Init, Burgos St., Valencia Negros Oriental | defective | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | defective | OK | For Rectification | For CSMP Endo | port holes for sealing | WACU | WACU | Off | fp-51qsxracconr19kedp1c | wcarp019ea |  | 51qsxraccon19kedm08pc-0642273 | 111626967 |  | Working | Working | None |  |  |  | generic, not used |  | working | Working | None | Powercity | Defective | Defective | 25 | Working | CF100 | working | Working | g2007263360 | Working | None |  |  | Working |  | Working | on going construction of genset pad and | BTS3012 | Retrieved |  | Off |  | Off |  | Off |  | Off |  |  | Off | For Rectification |  | Off |  | Off |  | Off |  | OK | OK | Ericsson | Minilink E | Yes |  |  | 0.90278 | OK | OK | No | V3665 Taclobo |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | No | Trad | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [100 empty] | Emerson | 53.9 | 0 | 4 | 4 | 3 | 2 | SacredSun | 150 | SacredSun | 150 |  |  |  |  | No |  | 53.9 | 53.9 |  |  | OK | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 16 |  | 16 | Exhaust fan | 16 | Ericsson Minilink E | 16 | [21 empty] | Eltek | [14 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 15 | 20 | Cabin light | 100 | Emerson Rectifier | 20 | Cabin CO | 30 | ACU1 | 30 | ACU2 | 20 | OB light | 20 | Perimeter light | 30 | Outdoor BTS 3012 | 20 | spare | 20 | Alarms | [20 empty] | Done | OK |  | AECabral III | March 07 2017 | ACU | 2 | defective WACUs | WFM | batteries | 2 | defective Narada 100 batteries | WFM | Kutai ATS (burnt) | 1 | Burnt kutai ATS | WFM | [28 empty] | Electromechanical | perimeter lights | 4 | n.a. | n.a. | n.a. | n.a. | Electromechanical | tower lights | 1 | n.a. | n.a. | n.a. | n.a. | Electromechanical | ATS | 1 | kutai | kutai | n.a. | for replacement (burnt)
V3712 SUN Tagbilaran Dao 2.pdf | V3712 | SUN Tagbilaran Dao 2 | 2017-02-07 | RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | 53.5 V, 36A | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy, Dao, Tagbilaran City | School | Lot | Permanent | Lot | Guyed 80ft | Van | 24hrs | Roving Guard | Yes |  | ATTY. DIONISIO D. BALITE |  | 123°51'38.83"E | 9°39'52.02"N |  | 2,0 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | For Rehab | OK | OK | OK | OK | OK | OK | 2,0 | OK | Ok | 0 | OK | OK | OK |  | WACU | Off | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C |  | 51PMXRACCAR19KEDT07PC-0500476 | 51PMXRACCAR19KEDN09PC-0437230 |  | Defective | Defective | None | 1.3 |  |  |  |  | 1,0 | None | None | TMEE | None | Working | 20 | Working | Off | 815 | Working |  | None | None |  | 19802-00 | Working |  | None |  | BTS3900A | Retrieved |  | Off | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN950 | No | 13108 | 12842 | -33.7 | OK | OK | Yes | Tagbilaran 1 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | V3712nTagbilaran Dao 2 2G | [41 empty] | 3 | V3712 SUN Tagbilaran Dao 2 3G | [66 empty] | Emerson | 53.5 |  | 36 |  | 5 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.4 | 53.3 | 53.3 | 53.2 | Off | 6 |  | 6 | RTN 950 Main (New) | 16 | RTN 950 Standby (New) | 16 | Huawei RTN (old) | 40 | WCDMA | 80 | 2G | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | BAU | [33 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 16.9 | 70 | Rectifier | 32 | ACU 1 | 20 | CO | 32 | ACU 2 | 20 | C. Light | 20 | OB Light | 20 | Alarm | 20 | P. Light | 20 | Spare | 20 | Spare | [20 empty] | Done | OK |  |  |  | Batteries | 12 | Vision CT12-100X | WFM
V3745 SUN Dumaguete City Looc 2 - Silliman Heights (1st Half) 2017v2.pdf | V3745 | SUN Dumaguete City Looc 2 (Silliman Heights) | 2017-02-09 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 6205-1 (V3745 Silliman Heights facing V0695 Silliman Medical) RTN620 ODU1 - 7038-1 (V3745 Silliman Heights facing V3665 Taclobo) RTN620 | OK |  | N/A |  | OK |  | OK |  | Rectification | ODU1 -42.5 (V3745 Silliman Heights facing V0695 Silliman Medical) RTN620 ODU1 -37.4 (V3745 Silliman Heights facing V3665 Taclobo) RTN620 | OK |  | OK | NOC PMR Ctrl# 17Q1-0697 | OK |  | N/A | outdoor site | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A | old genset not terminated | OK |  | OK |  | N/A |  | OK |  | OK |  | AECabral III | B | Feb 09 2017 | Purok 7, Upper Batinguel, Dumaguete City, Negros Oriental | Low land | within premise | Commercial | Inhouse B | guyed tower 150ft | none - outdoor | 24 / 7 | private lot with gate/fence | Yes | 2017 | CARMELITO S. CALUGCUGAN |  | 123.2758 | 9.3138 |  | no photocell but working | OK | OK | OK | For CSMP Endo | for grass cutting | Working | OK | OK | OK | OK | OK | OK | OK | None | OK | none - outdoor | OK | Ok | none - outdoor | OK | OK | For CSMP Endo | none - outdoor | WACU | WACU | Off | none - outdoor | none - outdoor |  |  |  |  | None | None | Off |  |  |  | none - outdoor | none - outdoor | WORKING but not terminated | None | None | Kohler | None | None | 10 KVA | Working | CF100 | working | Working | 212105686 | Working | None |  |  | For CSMP Endo |  | None | No ATS, old genset not terminated yet | BTS3900A GSM | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN620 | No | 14767 | 15187 | -42.5 | OK | OK | No | V0695 Silliman Medical | Huawei | RTN620 | No | 14823 | 15243 | -37.4 | OK | OK | No | V3665 Taclobo |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Aviat facing Mt Guihob | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | FE1 | V3745 3G | FE2 | V0695 3G | [16 empty] | V0695 Silliman Medical | FE1 | V0695 3G | [49 empty] | Huawei - APM30H | 53.7 | 0 | ?? | ?? | 2 | 2 | SacredSun | 180 | SacredSun | 180 |  |  |  |  | No |  | 53.8 | 53.8 |  |  | OK | 15 | CMUA | 15 | BBU | 15 |  | 15 |  | 5 |  | 5 |  | 5 |  | 5 |  | 20 | RRU 0 | 20 | RRU 1 | 20 | RRU 2 | 20 |  | 20 |  | 20 | [17 empty] | Huawei - APM30H | 53.8 | 0 | 4.7 | 4.7 | 3 | 2 | Narada | 100 | Narada | 100 |  |  |  |  | No |  | 53.5 | 53.8 |  |  | OK | 15 | DDCU | 15 | BBU | 15 | Alarms panel | 15 |  | 5 |  | 5 |  | 5 |  | 5 | [44 empty] | Off | [5 empty] | Off | [44 empty] | 60 | 15 | 20 |  | 20 | Perimeter light | 20 | Tower light | 20 | APMH 30 3G | 50 | APMH 30 2G | [30 empty] | Done | OK |  | AECabral III | 42765 | Batteries | 8 | Coslight 92X/H | WFM | Transformer | 1 | Transformer 10KVA | WFM | [32 empty] | ELECTROMECHANICAL | Perimeter lightings | 1 | n.a. | n.a. | 10watts | needs photocell | ELECTROMECHANICAL | Perimeter lightings | 1 | n.a. | n.a. |  | grounded
V3746 SUN Dumaguete City Bantayan - Bantayan (1st Half) 2017v2.pdf | V3746 | SUN Dumaguete City Bantayan - Bantayan | 2017-03-01 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 6832-1 (V3747 Motong facing V3746 Bantayan) RTN620 ODU1 - 6833-1 (V3747 Motong facing V3665 Taclobo) RTN620 ODU1 - a23104mk5h (V3747 Motong facing V3749 Batinguel) Minilink TN | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -35.4 (V3747 Motong facing V3746 Bantayan) RTN620 ODU1 -35.2 (V3747 Motong facing V3665 Taclobo) RTN620 ODU1 -23.5 (V3747 Motong facing V3749 Batinguel) Minilink TN | OK |  | OK | NOC PMR Ctrl# 17Q1-1188 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | 1-rectifier module for replacement | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | AECabral III | A | March 01 2017 | Jimenez Lot, Brgy. Bantayan, Dumaguete City, Negros oriental | Low land | within premise | Commercial | Inhouse A | SST 150ft 4L | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | SILLIMAN UNIVERSITY |  | 123.3058 | 9.3298 |  | working | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | defective | OK | OK | OK |  | WACU | WACU | Off | fp-51qsxracc0nr19keap1c | wconx019ed1 |  | 51qsxracc0n19keac10pc-0201574 | 51qsxracc0n19kedt15pc-0725330 |  | Working | Working | Off |  |  |  | Telecool FC-S |  | none | Working | None | none | None | Working | none | Working | CF100 | none | Working | 2004-248106 | None | None |  |  | Working |  | Working |  | BTS3012 | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN620 | No | 15327 | 14907 | -35.2 | OK | OK | No | V3747 Motong |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Emerson | 53.6 | 0 | 35 | 35 | 5 | 3 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 |  |  | No |  | 53.3 | 53.5 | 53.4 |  | OK | 16 |  | 16 |  | 16 |  | 25 | RTN | 10 |  | 10 | Fan | 10 | Fan Controller | 40 |  | 40 |  | 40 |  | 40 |  | 50 | 2G | 50 |  | 50 |  |  |  | 50 | 3G |  |  | 25 |  | 25 | [22 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 22 | 20 | Lighting | 60 | Emerson Rectifier | 20 | CO | 60 | Emerson Rectifier | 30 | ACU1 | 30 | ACU2 | 20 | OB Light | 20 | Perimeter light | 30 | spare | 20 | spare | 20 | spare | 20 | spare | [16 empty] | Done | OK |  | AECabral III | March 01 2017 | Narada Batteries | 8 | Narada 100 | WFM | Narada Batteries | 4 | Narada 150 | WFM | WACU | 1 | Condura | WFM
V3747 SUN Dumaguete City Looc 3 - Motong (1st Half) 2017v2.pdf | V3747 | SUN Dumaguete City Looc 3 - Motong | 2017-02-28 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 6832-1 (V3747 Motong facing V3746 Bantayan) RTN620 ODU1 - 6833-1 (V3747 Motong facing V3665 Taclobo) RTN620 ODU1 - a23104mk5h (V3747 Motong facing V3749 Batinguel) Minilink TN | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -35.4 (V3747 Motong facing V3746 Bantayan) RTN620 ODU1 -35.2 (V3747 Motong facing V3665 Taclobo) RTN620 ODU1 -23.5 (V3747 Motong facing V3749 Batinguel) Minilink TN | OK |  | OK | NOC PMR Ctrl# 17Q1-1146 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | Control module needs replacement (Mains alarms doesnt clear after commercial power resume) | OK |  | Rectification | 1 unit for OB light defective | OK |  | Rectification | no genset/ATS | OK |  | OK |  | OK |  | Rectification | grounded perimeter lights | OK |  | AECabral III | B | Feb 28 2017 | Purok Mabugnawon Brgy. Motong Dumaguete City | Low land | within premise | Commercial | Inhouse A | SST 150ft 4L | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | ABUNDIO LINAO SR. |  | 123.2861 | 9.3187 |  | grounded | For Repair | OK | OK | For CSMP Endo | grounded perimeter lights / on going genset pad construction | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | none | OK | OK | OK | on going installation of RTN facing V3749 Batinguel | WACU | WACU | Off | FP-51qsxracc0nr19kedp1c | FP-51pmxraccarp19kedp3c |  | 51qsxracc0n19kedf10pc-0328646 | 51pmxraccar19kedt07pc-0500860 |  | Defective | Working | Off |  |  |  | Telecool FC-S |  | none | Working | None | none | None | Working | none | Working | CF100 | none | Defective | ge04248155 | None | None |  |  | Working |  | Working | on going genset pad and day tank pedestal construction | BTS3012 | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN620 | No | 14907 | 15327 | -35.4 | OK | OK | No | V3746 Bantayan | Huawei | RTN620 | No | 14907 | 15327 | -35.2 | OK | OK | No | V3665 Taclobo | Ericsson | Minilink TN | No | 15327 | 14907 | -23.5 | OK | OK | No | V3749 Batinguel |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Emerson | 54.6 | 0 | 7 | 7 | 4 | 3 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 |  |  | No |  | 54.2 | 54.4 | 54.5 |  | OK | 40 | Vapel | 16 |  | 25 |  | 16 |  | 10 | RTN950 facing V3749 | 10 | Heat Extractor | 10 | Heat Extractor contorl unit |  |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 | [7 empty] | 25 | [7 empty] | Emerson Actura | 53.5 | 0 | 30 | 30 | 3 | 3 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 |  |  | No |  | 53.2 | 53.3 | 53.5 |  | OK | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 | 3G Node B | 40 | 2G BTS3012 | 10 | RTN950 facing V3749 | 40 | Vapel | 16 |  | 16 |  | 16 | [36 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 15 | 20 | Lighting | 60 | Emerson Rectifier | 20 | CO | 60 | Emerson Rectifier | 30 | ACU1 | 30 | ACU2 | 20 | OB Light | 20 | Perimeter light | 30 |  | 20 |  | 100 | Emerson Actura | 20 | [17 empty] | Done | OK |  | AECabral III | Feb 28 2017 | Narada Batteries | 16 | Narada 100 | WFM | Emerson Battery rack | 1 | Emerson Battery rack | WFM | [32 empty] | ELECTROMECHANICAL | Perimeter lightings | 1 | n.a. | n.a. | 10watts | grounded | Civil | Perimeter gate | 1 | n.a. | n.a. | n.a. | damaged | ELECTROMECHANICAL | TVSS | 1 | ASCO |  | 10w | damaged TVSS for OB light | ELECTROMECHANICAL | ACU | 1 | Carrier | FP-51qsxracc0nr19kedp1c |  | 51qsxracc0n19kedf10pc-0328646
V3748 SUN Dumaguete City Tabuctubig 2 - Mangnao (1st Half) 2017v2.pdf | V3748 | SUN Dumaguete City Tabuctubig 2 - Mangnao | 2017-03-02 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - 3593-1 (V3748 Mangnao facing V3665 Taclobo) RTN620 | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -34.8 (V3748 Mangnao facing V3665 Taclobo) RTN620 | OK |  | OK | NOC PMR Ctrl# 17Q1-1228 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | tower light not working | OK |  | Rectification | Photocell not working | OK |  | AECabral III | A | March 02 2017 | Purok Bayanihan, Brgy. Banilad, Dumaguete City, Negros Oriental | Low land | within premise | Commercial | Inhouse A | GT 100ft | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | ROEL T. CADAYDAY |  | 123.2939 | 9.291 |  | defective | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | none | OK | OK | For CSMP Endo | radio room floor needs cleaning | WACU | WACU | Off | cqxrt195ba | wconh019ed |  | 48403187 | 51qsxracc0n19kedk16pc-1074555 |  | Defective | Working | Off | [5 empty] | none | None | None | none | None | Defective | none | Working | CF100 | none | Working | 11031675 | None | None |  |  | Working |  | None |  | BTS3012 | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Huawei | RTN620 | No | 18635 | 19645 | -34.8 | OK | OK | No | V3665 Taclobo |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Emerson | 53.5 | 1 | 29 | 29 | 3 | 2 | SacredSun | 180 | SacredSun | 180 |  |  |  |  | No |  | 53.3 | 53.5 |  |  | OK | 16 |  | 16 |  | 40 | RTN | 40 |  | 6 |  | 6 |  | 50 | 2G | 50 |  | 50 |  | 50 |  | 50 | 3G | 6 | Rectifier controller | [35 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 18 | 70 | Emerson Rectifier | 30 | ACU | 20 | Cabin CO | 30 | ACU | 15 | Cabin lights | 15 | OB lights | 15 | Perimeter Lights | 20 | spare | 15 | spare | 20 | spare | [20 empty] | Done | OK |  | AECabral III | March 02 2017 | WACU | 2 | defective Condura WACUs | WFM | Mobile genset | 1 | defective Kohler 8.5KVA | WFM | [32 empty] | Electromechanical | perimeter lights | 2 | n.a. | n.a. | n.a. | n.a. | Electromechanical | tower lights | 1 | n.a. | n.a. | n.a. | n.a. | Eelctromechanical | ACU | 1 | Condura | cqxrt195ba | 2hp | 48403187
V3749 SUN Dumaguete City Poblacion No. 5 1 - Batinguel (1st Half) 2017v2.pdf | V3749 | SUN Dumaguete City Poblacion No. 5 1 - Batinguel | 2017-03-01 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK | ODU1 - a23104mk6p (V3749 Batinguel facing V3747 Motong) Ericsson TN | OK |  | N/A |  | OK |  | OK |  | OK | ODU1 -23.5 (V3749 Batinguel facing V3747 Motong) Ericsson TN | OK |  | OK | NOC PMR Ctrl# 17Q1-1172 | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | AECabral III | A | March 01 2017 | Poblacion No. 1 (Barangay 1), Dumaguete City, Negros Oriental | Low land | within premise | Commercial | Inhouse A | GT 150ft | collapsible van | 24 / 7 | private lot with gate/fence | Yes | 2017 | LUCIA A. GONZALES |  | 123.2855 | 9.3127 |  | defective | OK | OK | OK | OK | perimeter lights not working | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | defective | OK | Ok | defective | OK | OK | OK | on going installation of RTN facing V3747 Motong | WACU | WACU | Off | FP-51pmxraccarp19kedp3c | FP-51qsxracc0nnr19kedp1c |  | 51pmxraccar19kede08pc-0348074 | 51qsxracc0n19kedc10pc-0203880 |  | Working | Working | None | [5 empty] | none | None | None | none | None | Defective | none | Working | CF100 | none | Working | G-02551 | None | None |  |  | Working |  | Working |  | BTS3900A | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | Ericsson | Minilink TN | No | 14907 | 15327 | -23.5 | OK | OK | No | V3747 Motong |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | No |  |  |  | OK | OK | No |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 |  | 2 |  | 3 |  | 6 |  | 12 |  | 6 | [27 empty] | V3665 Taclobo | [20 empty] | V0695 Silliman Medical | [51 empty] | Emerson Actura | 53.5 | 0 | 26 | 26 | 3 | 4 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 | No |  | 53.2 | 53.5 | 53.2 | 53.4 | OK | 6 |  | 6 |  | 16 | Ericsson TN | 16 | RTN950 facing V3747 | 40 |  | 40 | 3G | 50 |  | 50 |  | 50 |  | 50 | 2G | 50 |  | 50 |  | 6 | Rectifier controller | [33 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 15 | 70 | Rectifier | 30 | ACU1 | 20 | CO | 30 | ACU2 | 15 | Cabin lights | 15 | OB lights | 15 | Perimeter lights | 20 | spare | 15 | spare | 20 | spare | [20 empty] | Done | OK |  | AECabral III | March 01 2017 | Narada Batteries | 8 | Narada 100 | WFM | WACU | 1 | Carrier fp-51pmxraccarp19kedp3c / 51pmxraccar19kedc08pc-0178579 | WFM | [32 empty] | Electro Mechanical | Perimeter lights | 1 | n.a. | n.a. | n.a. | defective
V4256 SUN Dimiao_Poblacion_2_28_17.pdf | V4256 | SUN DIMIAO_POBLACION | 2017-02-28 | FHG/RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro installed | OK |  | N/A | CEN Transport, no MW installed. | N/A | CEN Transport, no MW installed. | OK |  | OK |  | OK | 3G xml | N/A | CEN Transport, no MW installed. | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro installed | N/A | No Bro installed | OK |  | Off | CEN Transport, no MW installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK | Passed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Dimiao, Bohol | Residential | Lot | Permanent | Lot | Guyed Monopole / 150 Ft. | Collapsible | 24 Hrs. | None | Yes |  | Justiniano Ydulzura | 9228918006 | 124° 09’ 42.3” | 09° 36’ 26.5” | Brgy. Poblacion, Dimiao, Bohol | 42767 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36557 | OK | Ok | 0 / 0 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCAR19KEDP3C | FP-51PMXRACCAR19KEDP3C |  | 51PMXRACCAR19KEDT09PC-0529993 | 51PMXRACCAR19KEDT09PC-0537731 |  | Defective | Working | Off |  | 7.8A |  |  |  | 36526 | Off | Off | Denyo | Working | Working | 25 | Working | Off | 221.1 | Working | 12653371 | None | None | 200 li plus 15 inches | 2020010967 | Working | None | None | No exhaust fan installed. | BTS 3900A | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK |  |  | No |  |  |  | Off | Off | No |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | NE40E-X2 | Yes | Off | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off | CEN Transport, no MW installed. | Huawei CEN NE40E-X2 | 1 | Dimiao 2G-1800 1st E1 | 2 | Dimiao 2G-1800 2nd E1 | 3 |  | 4 |  | 5 |  | 6 | [27 empty] | Huawei CEN ATN 950 | 1 | 0/2/5 Dimiao 3G-2100 | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | [57 empty] | Emerson | 53.5V | 0.0A | 8.0A | 8.0A | 5 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.2V | 53.2V | 53.2V |  | OK | 6 | BAU | 6 |  | 16 |  | 16 |  | 40 | NE40E-X2 Main | 80 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 50 |  | 6 | [19 empty] | Eltek | 54.55V | 0.0A | 35.0A | 35.0A | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 50.6V | 50.6V | 50.6V |  | Off | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | NE40E-X2 Redundant | 40 |  | 40 | 3G-2100 DCDU | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 80 | BTS 3900A | [15 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 20.6 | 70 | EMERSON | 32 | ACU 1 | 20 | C. O. | 32 | ACU 2 | 20 | CABIN LIGHT | 20 | TOWER LIGHT | 20 | ALARM | 20 | PERIMETER LIGHT | 70 | ELTEK 1 | 20 | ELTEK 2 | [20 empty] | Done | OK |  |  |  | Rectifier Batteries | 12 | Vision / 12V, 100AH | WFM, FO | [36 empty] | Electromechanical | ACU | 1 | Carrier | FP-51PMXRACCAR19KEDP3C | 2HP | 51PMXRACCAR19KEDT09PC-0529993 | Electromechanical | Perimeter Light (busted CFL) | 1 | [81 empty] | ACU with defective dual capacitor and perimeter light with busted CFL
V4258 Sun Dauin First Half 2017 PMR v2.pdf | V4258 | SUN DAUIN | 2017-03-01 | KTA | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | POBLACION, DAUIN, NEGROS ORIENTAL | RESIDENTIAL | GREENFIELD | PERMANENT | LOT | SST / 42M | VAN | 24 HOURS | CARETAKER | Yes | [6 empty] | WO / 2/4 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | DEF / 1/1 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED B15PC - 0154320 | 51QSXRACCON19KEDC10PC - 0193740 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | POWERCITY | Working | Working | 25 | Working | CF200 | 1590 | Working | 208NM014821 | Working | None | 2000 Li |  | Working | 0 | Working |  | BTS3900L | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off | BOSER | 6 | Retrieved | None |  | Off | BBU3900 | Retrieved |  | Off |  | OK | OK | HARRIS | STRATEX | Yes | 7240 | 7401 | 0.91388 | OK | OK | Yes | 4217 BACONG | HARRIS | STRATEX | Yes | 7513 | 7681 | 1.1473 | OK | OK | Yes | V4262 SUN ZAMBOANGUITA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK | 54.07 | 1 | 1 | 54 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 53.05 | 54.45 | 54.01 |  | OK | [8 empty] | 63A | 3G | 63A | LTE TD |  |  | 63A | UPPER | 63 | LOWER |  |  | 40 | BRO |  |  |  |  | 40 | DCPDB PROT | [16 empty] | EMERSON | 54.93 | 0 | 4 | 4 | 3 | 3 | NARADA | 105 | NARADA | 105 | NARADA | 105 |  |  | No |  | 54.9 | 54.7 | 54.7 |  | Off | [8 empty] | 63 | DCPDB MAIN | [49 empty] | No | [5 empty] | Off | [44 empty] | 150 | 150 | 20 | L.O |  |  | 70 | RECTIFIER |  |  | 20 | C.O |  |  | 30 | ACU 1 |  |  | 30 | ACU 2 |  |  | 20 | ALARM |  |  | 20 | OB LIGHT |  |  | 20 | P.L |  |  | 70 | NO LABEL |  |  | 70 | NO LABEL |  |  | Done | OK
V4262 Sun Zamboanguita First Half 2017 PMR v2.pdf | V4262 | SUN ZAMBOANGUITA | 2017-03-07 | KTA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | POBLACION, ZAMBOANGUITA, NEGROS ORIENTAL | RESIDENTIAL | GREENFIELD | PERMANENT | LOT | SST / 42M | VAN | 24 HOURS | CARETAKER | Yes | [6 empty] | WO / 1/4 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WO | OK | Ok | DEF / 1/1 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED K16PC - 1074187 | 51QSXRACCON19KED K15PC - 0540081 |  | Working | Working | Off | 8.4 | 8.4 |  | NA | NA | WO | None | None | POWERCITY | Working | Working | 25 | Working | CF200 | 5788 | Working |  | Working | None | 2000 Li |  | Working | 0 | Working |  | BTS3012 | Retrieved | BTS3900L | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | V4258 SUN DAUIN | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | 5855 ANTULANG |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Yes | Trad | Yes |  |  | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | NOKIA | 54.46 | 0.3 | 44.2 | 43.8 | 6 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 |  |  | No |  | 53.4 | 54.45 | 54.47 |  | OK | [8 empty] | 40 | DCPDB Main | [12 empty] | 40 | UPPER GSM | 40 | LOWER GSM | 40 | DCPDB PROT | [16 empty] | EMERSON | 53.5 | 0 | 3 | 3 | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No |  | 53.4 | 53.5 |  |  | Off | [10 empty] | 40 | DCPDB MAIN | [47 empty] | No | [5 empty] | Off | [44 empty] | 150 | 150 | 20 | L.O |  |  | 70 | RECTIFIER |  |  | 20 | C.O |  |  | 30 | ACU 1 |  |  | 30 | ACU 2 |  |  | 20 | OB LIGHT |  |  | 20 | P.L. |  |  | 20 | SPARE |  |  | 70 | SPARE |  |  | 70 | EMPOWER RECTIFIER |  |  | Done | OK
V4330 SUN Sagbayan_3_16_17.pdf | V4330 | SUN SAGBAYAN | 2017-03-16 | FHG/MRR | OK |  | N/A |  | OK |  | N/A |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | OK |  | OK |  | OK |  | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | OK |  | OK |  | Rectification | Genset is defective, already requested repair. No ATS is installed. | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Brgy. Poblacion, Sagbayan, Bohol | Residential | Lot | Permanent | Lot | 4L-SST and 150 Ft. | Collapsible | 24 Hrs. | Caretaker | Yes |  | Jimmy Torrefranca | 9228277549 | 124° 05’ 32.6” | 09° 54’ 32.6” | Brgy. Poblacion, Sagbayan, Bohol | 42737 | For Repair | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | Expired | OK | 36557 | OK | Ok | None | OK | OK | For CSMP Endo |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C |  | 51PMXRACCARP19KEDT09PC-0529998 | 51PMXRACCARP19KEDT09PC-0537710 |  | Working | Working | Off | 7.0A | 7.1A |  |  |  | 0 / 1 | None | None | Denyo | None | Off | 25 | Working | Off | 105.5 | Working | 9651448 | Defective | None | 450 | 303030649 | For CSMP Endo | None | None | No exhaust fan is installed. | BTS 3900L | Retrieved | BTS 3900L | Retrieved | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 8207.27 | 7895.95 | -36 | OK | OK | No | 3311-Catigbian |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | 3311-Catigbian | 1 | Sagbayan 2G 1st E1 | 2 | Sagbayan 2G 2nd E1 | 3 |  | 4 | [31 empty] | 3311-Catigbian | 1 | Sagbayan 3G-2100 3G | 2 |  | 3 |  | 4 | [65 empty] | Emerson | 53.5V | 0.0A | 41.0A | 41.0A | 5 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 53.3V | 53.3V | 53.3V |  | OK | 80 |  | 16 |  | 16 | RTN facing Catigbian Main | 40 | BTS 3900L Upper | 40 | BTS 3900L Lower | 50 | 3G-2100 DCDU | 50 | RTN facing Catigbian Rdnt | 50 |  | 50 |  | 50 |  | 50 |  | 6 | BAU | [35 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 24.1 | 70 | Emerson Rectifier | 32 | ACU 1 | 20 | Lightings | 32 | ACU 2 | 20 | C. O. | 20 | O. B. Light | 20 | Perimeter Lights | 20 | Spare | 20 | Spare | 20 | Spare | [20 empty] | Done | OK |  |  |  | MW Antennas | 2 units | Ericsson / 1.2m diameter | FO
V4386-SUN AYUNGON-031517.pdf | V4386 | Sun Ayungon Tampocon | 2017-03-15 | rdcueco | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | Rectification | For rectification c/o Huawei. Under project UNO(17Q1-1548) | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | for rectification c/o Huawei.Under project UNO | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  |  | B |  | Brgy Nabalabag Pamplona Negros Oriental | Commercial | Lot | Permanent | Lot | 150 ft SST | Van | 24 hrs | Caretaker | Yes | [7 empty] | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | For Rehab |  | OK | For Rectification | OK |  | WACU | Off | Off | 51PMXRACCAR19KEDN07PC | 51qsxracc0n19kedB13pc |  | 376548 | 61431 |  | Defective | Working | Off |  |  |  | NA | NA |  | Off | Off |  | Working | None |  | Working | CF100 |  | Working |  | None | None |  |  | Working |  | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off | NA | Off | NA |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | ERICSSON | MLTN | No | 8482 | 8363 | -35 | OK | OK | Yes | 4215 TAYASAN |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Yes |  |  |  | Off | Off | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | EMERSON | 54 | 0 | 36 |  | 3 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN |  | No | [5 empty] | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | OK | 50 |  | 50 |  | 63 |  | 63 |  | 50 |  | 40 |  | 16 |  | 16 |  | 16 |  | 10 |  | 10 |  | 10 |  | 10 |  | 6 |  | 6 |  |  |  | 80 |  |  |  | 80 | [22 empty] | Off | [5 empty] | Off | [44 empty] | 150 |  | 50 | POWER ONE | 40 | ACU1 | 40 |  | 40 | ACU2 | 40 |  | 40 | ELTEK 2 | 30 | CO | 20 | PERIMETER LIGHT | 70 | ELTEK | 30 | SPARE | [20 empty] | Done | OK
V5058 Sevilla.pdf | V5058 | Sevilla | 2017-02-09 | RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  |  | Off |  | Brgy. Kabankalan, Sevilla, Bohol | Residential | Lot | Permanent | Lot | 150ft Guyed | NA | 24hrs | Caretaker | Yes |  | Feliciana Gumapac | 9183224607 | 124.0516 | 9.6985 | Brgy. Kabankalan, Sevilla, Bohol | 3,1 | OK | OK | for Replacement | OK |  | Defective | OK | OK | OK | OK | OK | OK | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | 1,0 | None | None | DENYO | Working | None | 25 | Working | CF100 | 299.5 | None | 2356566 | None | None |  | 2525020145 | Off |  | Off |  |  | Off | BTS3900A | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | NOKIA | FLEXIHOPPER | No | 7142000 | 7303000 | -61 | OK | OK | No | Loboc |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | NOKIA FLEXIHOPPER | 1 | Sevilla 2G | 8 | Sevilla 3G 1st E1 | 9 | Sevilla 3G 2nd E1 | 10 | Sevilla 3G 3rd E1 | 11 | Sevilla 3G 4thE1 | [101 empty] | Huawei |  |  |  |  | 3 | 2 | Shoto | 90 | Shoto | 90 |  |  |  |  | No |  | 49.7 | 49.6 |  |  | OK | 15 | NOKIA FH | 15 | FAN02A | 15 | 2G BBU | 15 | BATTERY FAN | 15 | 3G BBU | 15 | RRU 2 | 15 | RRU 1 | 5 | RRU 0 | [43 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 70 | 7.4 | 50 | BTS3900A | 20 | Tower Light | 20 | PERIMETER LIGHT | 20 | C.O. |  |  | 63 | SPARE | [28 empty] | Done | OK | [43 empty] | ELECTROMECHANICAL | TOWER LIGHTING | [5 empty] | CIVIL | GATE PADLOCK | 1
V5183 Mabini Cabulao .pdf | V5183 | Mabini Cabulao | 2017-03-29 | RSJ/GZG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | IF CABLE FOR RE-GROOMING | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  |  | Off |  | Brgy San Roque (Cabulao), Mabini, Bohol | Residential | Outdoor Site | Permanent | Lot | SST 150ft | Outdoor | 24 Hrs | N/A | Off |  | Amora |  | 124.5235 | 9.9064 | Brgy San Roque (Cabulao), Mabini, Bohol | 2,0 | OK | OK | OK | OK |  | Working | OK | OK | OK | For Grooming | OK | OK | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | NONE | None | None |  | None | None |  | Working | Off |  | Working | 100501016941 | None | None |  |  | Off |  | None |  |  | Off | BTS3900A | Retrieved |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes | 7373 | 7177 | 0.12823 | Off | Off | Yes | MAASIN |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | RTN 950 | 1 | MABINI CABULAO 2G 1ST E1 | [109 empty] | ELTEK | 53.45 | 0 | 14 |  | 4 | 4 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | No |  | 51.1 | 51.1 | 51.1 | 51.2 | OK | 100 | BTS3900A | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 16 |  | 16 | RTN MAASIN A | 16 | [19 empty] | HUAWEI | 53.5 | 0 | 4.1 |  | 2 | 2 | SACRED SUN | 150 | SACRED SUN | 150 |  |  |  |  | No |  | 51.9 | 51.9 |  |  | OK | 16 |  | 16 |  | 16 | RTN MAASIN B | 32 |  | 32 |  | 32 |  | 63 |  | 63 |  | 20 |  | 20 |  | 32 |  | 32 |  | 63 |  | 63 |  | 80 |  | 80 | [28 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 5.8 | 20 | TVSS | 20 | C.O. | 50 | HUAWEI RECTIFIER | 20 | SHELTER LIGHT | 20 | TOWER LIGHT | 20 | PERIMETER LIGHT | 50 | ELTEK 2 | 70 | ELTEK 1 | [24 empty] | Done | OK |  |  |  | BATTERIES | 8 | NARADA 12V 100AH | FO & WFM | [36 empty] | CIVIL | GATE | [5 empty] | CIVIL | MCB AND MTS CORRODED | [5 empty] | ANTENNA SYSTEM | GROUNDING KIT | [5 empty] | ANTENNA SYSTEM | IF CABLE RE-GROOMING
V5248 Guihulngan Hilaitan (1st Half) 2017v2-.pdf | V5248 | Guihulngan Hilaitan | 2017-01-24 | ASLCal | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | Rectification | ODU1 - 23 RTN ODU2 - 654-8 RTN ODU1 - -44.8 Ericsson TN ODUs no grounding | OK |  | N/A |  | OK |  | OK |  | OK | -35.5 / -38.4 SD RTN facing Aloguinsan -44.8 Ericsson TN facing Hilaitan Sun | OK |  | OK | NOC PMR Ctrl# 17Q1-0324 | OK |  | N/A | outdoor site / FTK | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | huawei - 22.4A | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | No tower grounding (w/ history of grounding theft) | N/A | outdoor site | OK |  | OK |  | AECabral | A | Jan 24 2017 | Brgy Hilaitan, Guihulngan, Negros Oriental | Highland | None | Commercial | Inhouse B | SST 150ft | Open shelter | 24hrs | Uphill | Yes | 2017 |  |  | 123.313439° | 10.232861° |  | Breaker tripped off upon our arrival | For Repair | OK | OK | For CSMP Endo | for grass cutting | Defective | OK | OK | OK | OK | For Rehab | For Rectification | OK | None | OK | defeictive | OK | Ok | none | OK | OK | OK | lights need checking | Off | Off | Off | [6 empty] | None | None | None | [5 empty] | None | Off | Off |  | Off | Off |  | Off | Off |  | Working |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 1 | 2G | 2 | Hilaitan Sun 2G DCS | [122 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off | [43 empty] | Antenna Sys | ODU grounding | 30mtrs | n.a. | n.a. | n.a. | n.a. | Electro Mech | tower bus bar grounding | 150ft | n.a. | n.a. | n.a. | n.a. | Electro Mech | Tower Grounding cable | 180ft | n.a. | n.a. | n.a. | n.a.
V5291 Tagb_Mansasa.pdf | V5291 |  | 2017-01-20
V6603 Tagbilaran Alturas Mall_3_14_17.pdf | V6603 | TAGBILARAN ALTURAS MALL | 2017-03-14 | FHG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | No Bro is installed. | OK |  | OK |  | OK |  | N/A | IBS site | N/A | IBS site | OK | 3G xml | OK |  | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A | No Bro is installed. | N/A | No Bro is installed. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | See page 5. | OK |  | N/A |  | OK |  | N/A | No genset/ATS is installed. IBS site, tapped to Mall. | OK |  | N/A | No tower is installed, IBS iste. | OK |  | OK |  | OK |  |  | Off |  | CPG Avenue, Tagbilaran City, Bohol | Commercial | Roof Deck | Tapped to Building | Building | IBS Site, no tower | Collapsible | Mall Hours | Admin/Bldg Security | Yes |  | Alturas Supermarket Corporation | Edith Ararao / 09175304259 | 123.856 | 9.6434 | CPG Avenue, Tagbilaran City, Bohol | N / A | Off | Off | Off | Off | IBS site, radio room located on roof deck | Off | OK | OK | OK | OK | Off | OK | OK | None | OK | 36617 | OK | Ok | 36526 | OK | OK | Off | For deployment of fire extinguisher | WACU | WACU | Off | WCONH019EE | WCONH019EE |  | 51QSXRACCON19KEEA16PC-0066567 | 51QSXRACCON19KEEA16PC-0066566 |  | Working | Working | Off | 7.0A | 7.4A |  |  |  |  | None | None |  | None | Off |  | None | Off |  | None | 9582722 | Off | None | N / A |  | Off | N / A | Off | IBS site, no genset/ATS/fuel tank installed. Tapped to Mall. |  | Off |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK | Huawei | RTN 950 | No | 7614.5 | 7453..00 | -34.1 dBm | OK | OK | No | 794-Tagbilaran 3 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing Tagbilaran 3 | 1 |  | 2 | no 2G is installed | 3 |  | 4 | [31 empty] | facing Tagbilaran 3 | 1 | Alturas 3G-2100 | 2 |  | 3 |  | 4 | [65 empty] | Eltek | 54.07V | 0.0A | 12.0A | 12.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.8V | 53.8V | 53.8V | 53.8V | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 | 3G Breaker | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 | RTN facing Tagbilaran 3 Rdnt | 16 | RTN facing Tagbilaran 3 Main | [15 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 16 | 50 | Eltek 1 | 50 | Eltek 2 | 40 | ACU 1 | 40 | ACU 2 | 20 | Convenience Outlet | 20 | Lightings | 20 | Spare | 20 | Spare | 20 | Spare | 20 | Spare | [20 empty] | Done | OK | [128 empty] | IBS site, only MW is mounted outdoor. |  |  |  |  | Tapped to Building
Z80 Plaza Marcela_1_9_17.pdf | Z80 | PLAZA MARCELA | 2017-01-09 | FHG/MRR/RSJ | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A | CEN Transport | N/A | CEN Transport | N/A | IBS site | N/A | IBS site | Off | Only 2G equipment is installed. | N/A | CEN Transport | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A | CEN Transport | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek: 54.2V, 54.2V, 54.2V, 54.2V | OK | Passed. | N/A |  | OK | Tapped to Mall. No ATS/MTS installed. | N/A | Tapped to Mall. No ATS/genset installed. | OK | Tapped to Mall | N/A | IBS site, no tower installed. | OK |  | OK |  | OK |  |  | Off |  | Corner Pamaong and Belderol Sts., Brgy. Cogon, Tagbilaran City, Bohol | Commercial | Roofdeck | Tapped to Mall | Building | IBS Site, no tower | Collapsible | Mall Hours | With access pass | Yes |  | Alturas Supermarket Corporation | (038) 412 5867 | 123° 51.086' | 09° 39.094' | Corner Pamaong and Belderol Sts., Brgy. Cogon, Tagbilaran City, Bohol | N/A | N/A | N/A | OK | Off | IBS site, roof deck location. | Off | Off | Off | Off | Off | Off | Off | For Rehab | OK | OK | 2000-04-01 | OK | Ok | 0/1 | OK | OK | OK | Flooring for slight repair. | WACU | WACU | Off | FP-51QSXRACCONR19KEDP1C | FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDA10PC-0003047 | 51QSXRACCON19KEDB09PC-0093203 |  | Working | Working | Off | 7.7A | 7.0A |  |  |  | N/A | None | None | N/A | None | None | N/A | None | Off | N/A | None | 865-283 | None | None | N/A |  | Off | N/A | None | IBS site, tapped to building. No ATS/genset installed. | BTS 3900 | Retrieved |  | Off |  | Off |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | ATN 950B | Yes | Off | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 | 2G-1800 1st E1 | [36 empty] | Huawei CEN | [72 empty] | Eltek | 54.22V | 0.0A | 6.0A | 6.0A | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.2V | 54.2V | 54.2V | 54.2V | OK | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 | ATN 950B (A) | 16 | ATN 950B (B) | 80 | BTS 3900 | [15 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 70 | 13 | 50 | SPARE | 70 | ELTEK 2 | 20 | SPARE | 30 | ACU 1 | 30 | ACU 2 | 20 | C. O. | 20 | SPARE | 70 | ELTEK 1 | [24 empty] | Done | OK |  |  |  | Rectifier Cabinet | 1 | PSSS Rectifier / SN: 589584 | WFM, FO | [36 empty] | Civil | Others(Shelter Flooring)) | [83 empty] | IBS site, no tower installed. |  |  |  |  | IBS site, tapped to Mall. No genset/fuel tank installed. | Floor for slight repair.
Z82 BQ Mall_1_11_17.pdf | Z82 | BOHOL QUALITY MALL | 2017-01-11 | FHG/RSJ | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A | CEN Transport | N/A | CEN Transport | N/A |  | N/A | IBS site | OK |  | N/A | CEN Transport | OK |  | OK | w/ NOC | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A | CEN Transport | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Eltek: 54.2V, 54.2V, 54.2V | OK | Passed. | N/A |  | OK | Tapped to Mall. IBS site, no ATS/MTS installed. | N/A | Tapped to Mall. IBS site, no ATS/genset installed. | OK | Tapped to Mall. | N/A | IBS site, no tower installed. | N/A | Shelter flooring for rehab. | OK |  | OK |  |  | Off |  | CPG Avenue, Brgy. Pob. 1, Tagbilaran City, Bohol | Commercial | Basement 3 | Tapped to Mall | Building | IBS Site | Collapsible | Mall Hours | With access pass | Yes |  | Bohol Quality Corporation | (038) 412 3964 | 123° 51’ 23.1” | 09° 38’ 34.7” | CPG Avenue, Brgy. Pob. 1, Tagbilaran City, Bohol | N/A | N/A | N/A | OK | Off | IBS site, Basement 3 location. | Off | Off | Off | Off | Off | Off | Off | For Rehab | Off | Off | 4 | Off | Off |  | Off | Off | Off |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDT15PC-0722213 | 51QSXRACCON19KEDM14PC-0516754 |  | Working | Working | Off | 6.7 | 7.1 |  |  |  | N/A | None | None | N/A | None | None | N/A | None | Off | N/A | None |  | None | None | N/A | 001-901-673-000 | Off | N/A | None | IBS site, no genset/ATS/fuel tank installed. Tapped to Mall. | BTS 3900 | Retrieved |  | Off | BBU 3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off | Normal status | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | Huawei | ATN 950B | No | Off | No |  |  | Off | Off | Off |  |  | Off | Off | Off |  | Huawei CEN | 1 | 2G-1800 1st E1 | [36 empty] | Huawei CEN | 1 |  | 2 |  | 3 | 3G-2100 | [66 empty] | Eltek | 54.63V | 0.0A | 11.0A | 11.0A | 4 | 4 | Lynx | 170 | Lynx | 170 | Lynx | 170 | Lynx | 170 | No |  | 54.8V | 54.8V | 54.8V | 54.8V | OK | 100 |  | 100 |  | 100 |  | 100 |  | 80 |  | 80 |  | 80 |  | 80 | BTS 3900 2G-1800 | 63 | BTS 3900 3G-2100 | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 | ATN 950B (A) | 20 | ATN 950B (B) | 10 |  | 10 | [16 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 10 | 50 | SPARE | 30 | ELTEK 2 | 50 | ELTEK 1 | 30 | SPARE | 30 | ACU 1 | 30 | ACU 2 | 20 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SPARE | 20 | CABIN LIGHTS | 20 | C.O. | [16 empty] | Done | OK | [43 empty] | Civil | Others (Shelter Flooring) | 1 Lot | [82 empty] | IBS site, no tower installed. |  |  |  |  | IBS site, tapped to Mall. No genset/fuel tank installed.