## NCebu
| Site No | Site Name | PMR Date | FO Engineer | VSWR | VSWR Remarks | Combiner | Combiner Remarks | Grounding | Grounding Remarks | VSAT(Outdoor) | VSAT(Outdoor) Remarks | GPS Antenna and Cable | GPS Antenna and Cable Remarks | Outdoor FTP/STP Cable and RJ45 Connector | Outdoor FTP/STP Cable and RJ45 Connector Remarks | Feeder Cable | Feeder Cable Remarks | ODU and Cables | ODU and Cable Remarks | Radio ODU | RADIO ODU Remarks | Access Point | Access Point Remarks | Antenna (Panel) | Antenna (Panel) Remarks | Backup of XML/Config | Backup of XML/Config Remarks | Microwave RSL | Microwave RSL Remarks | Equipment Label | Equipment Label Remarks | Equipment Housekeeping | Equipment Housekeeping Remarks | Equipment Grounding | Equipment Grounding Remarks | Indoor Cable | Indoor Cable Remarks | Indoor FTP/STP Cable and RJ45 Connector | Indoor FTP/STP Cable and RJ45 Connector Remarks | Surge Suppressor | Surge Suppresor Remarks | CMM/Router | CMM/Router Remarks | 19in Rack | 19in Rack Remarks | Radio IDU | Radio IDU Remarks | Multiplexer | Multiplexer Remarks | ODF Patch Panel | ODF Patch Panel Remarks | Leased Cable Facility | Leased Cable Facility Remarks | VSAT(Indoor) | VSAT(Indoor) Remarks | Synchronization | Synchronization Remarks | DC Power Plant(Rectifiers) | DC Power Plant(Rectifiers) Remarks | Battery Discharge Test | Battery Discharge Test Remarks | TVSS and Surge Protection | TVSS and Surge Protection Remarks | AC Power Plant | AC Power Plant Remarks | Genset and ATS | Genset and ATS Remarks | Commercial Power Line/Wind and Solar Power | Commercial Power Line/Wind and Solar Power Remarks | Tower | Tower Remarks | Radio Room | Radio Room Remarks | Premise | Premise Remarks | Site Photo | Site Photo Remarks | Reviewed By Supervisor | Site Class | Date | Site Address | Site Category | Radio Room Location | Power Type | Site Type | Tower Type and Height | Shelter Type | Access Hours | Entry Method | NTC License Posting | Valid Until | Lessor's Name | Lessor's Contact No | Longitude | Latitude | Lessor's Address | Perimeter Lights | Gate Status | Perimeter Wall/Fence Status | Padlock Status | Perimeter Area Cleanliness | Perimeter and Premise Remarks | Tower Light | Antenna Condition | MW LOS Checking | Lightning Arrester | Tower Cable Grooming | Tower Grounding | Bus Bar Termination | Shelter Wall/Flooring Condition | Fire Extinguisher | Shelter Cable Tray | Shelter Lighting Fixtures | Shelter Cable Grooming | Shelter Grounding | Shelter Emergency Lights | Shelter Cable Labeling | Port Hole Sealing | Shelter Cleanliness | Shelter Remarks | ACU 1 Type | ACU 2 Type | ACU 3 Type | ACU 1 PN/Model | ACU 2 PN/Model | ACU 3 PN/Model | ACU 1 SN | ACU 2 SN | ACU 3 SN | ACU 1 Status | ACU 2 Status | ACU 3 Status | ACU 1 Ampere Reading | ACU 2 Ampere Reading | ACU 3 Ampere Reading | Exhaust Fan 1 PN/Model | Exhaust Fan 2 PN/Model | Genset | Exhaust Fan 1 Status | Exhaust Fan 2 Status | Genset Brand | ATS | ACU Controller | Genset Rating | MTS | Electric Meter CF Rating | Genset Running Hours | TVSS/Surge Suppressor | Electric Meter No | Day Tank Status | Illegal Tapping | Reserve Diesel (in Liters) | Electric Bill SIN No | Genset Warm Up | No of Empty Drums | Genset Base Pad | Support Facilities Remarks | 2G 1800 Eqpt | 2G 1800 SN/SCF | 2G 900 Eqpt | 2G 900 SN/SCF | 3G 2100 Eqpt | 3G 2100 SN/XML | 3G 850 Eqpt | 3G 850 SN/XML | Wimax No. of CAP | Wimax SN | BRO Router | BRO No. of AP | BRO SN | BTS Alarms Clearing | FD LTE Eqpt | FD LTE SN/XML | TD LTE Eqpt | TD LTE SN/XML | Metro Wifi No. of AP | Metro Wifi SN | BTS Remarks | Eqpt Cleaning | Eqpt Label | MW 1 Brand | MW 1 Model | MW 1 Protected | MW 1 UL Freq | MW 1 DL Freq | MW 1 RSL | MW 1 LOS | MW 1 Card Tag | MW 1 Dual Feed | MW 1 Facing | MW 2 Brand | MW 2 Model | MW 2 Protected | MW 2 UL Freq | MW 2 DL Freq | MW 2 RSL | MW 2 LOS | MW 2 Card Tag | MW 2 Dual Feed | MW 2 Facing | MW 3 Brand | MW 3 Model | MW 3 Protected | MW 3 UL Freq | MW 3 DL Freq | MW 3 RSL | MW 3 LOS | MW 3 Card Tag | MW 3 Dual Feed | MW 3 Facing | MW 4 Brand | MW 4 Model | MW 4 Protected | MW 4 UL Freq | MW 4 DL Freq | MW 4 RSL | MW 4 LOS | MW 4 Card Tag | MW 4 Dual Feed | MW 4 Facing | MW 5 Brand | MW 5 Model | MW 5 Protected | MW 5 UL Freq | MW 5 DL Freq | MW 5 RSL | MW 5 LOS | MW 5 Card Tag | MW 5 Dual Feed | MW 5 Facing | VSAT Brand | VSAT model | VSAT Protected | VSAT UL Freq | VSAT DL Freq | VSAT RSL | VSAT LOS | VSAT EB/NO | VSAT Dual Feed | VSAT Facing | Line Driver 1 NE | Line Driver 1 Carrier | Line Driver 1 Brand | Line Driver 1 PL No./Ckt No | Line Driver 2 NE | Line Driver 2 Carrier | Line Driver 2 Brand | Line Driver 2 PL No./Ckt No | Line Driver 3 NE | Line Driver 3 Carrier | Line Driver 3 Brand | Line Driver 3 PL No./Ckt No | Optical Tx 1 Eqpt Brand | Optical Tx 1 Model | Optical Tx 1 Protected | Optical Tx 1 FOC | Optical Tx 1 Dual Feed | Optical Tx 2 Eqpt Brand | Optical Tx 2 Model | Optical Tx 2 Protected | Optical Tx 2 FOC | Optical Tx 2 Dual Feed | Optical Tx 3 Eqpt Brand | Optical Tx 3 Model | Optical Tx 3 Protected | Optical Tx 3 FOC | Optical Tx 3 Dual Feed | Tx Remarks | E1 Inventory 1 | E1 Inventory 1 Port 1 | E1 Inventory 1 Ckt Assignment 1 | E1 Inventory 1 Port 2 | E1 Inventory 1 Ckt Assignment 2 | E1 Inventory 1 Port 3 | E1 Inventory 1 Ckt Assignment 3 | E1 Inventory 1 Port 4 | E1 Inventory 1 Ckt Assignment 4 | E1 Inventory 1 Port 5 | E1 Inventory 1 Ckt Assignment 5 | E1 Inventory 1 Port 6 | E1 Inventory 1 Ckt Assignment 6 | E1 Inventory 2 | E1 Inventory 2 Port 1 | E1 Inventory 2 Ckt Assignment 1 | E1 Inventory 2 Port 2 | E1 Inventory 2 Ckt Assignment 2 | E1 Inventory 2 Port 3 | E1 Inventory 2 Ckt Assignment 3 | E1 Inventory 2 Port 4 | E1 Inventory 2 Ckt Assignment 4 | E1 Inventory 2 Port 5 | E1 Inventory 2 Ckt Assignment 5 | E1 Inventory 2 Port 6 | E1 Inventory 2 Ckt Assignment 6 | E1 Inventory 3 | E1 Inventory 3 Port 1 | E1 Inventory 3 Ckt Assignment 1 | E1 Inventory 3 Port 2 | E1 Inventory 3 Ckt Assignment 2 | E1 Inventory 3 Port 3 | E1 Inventory 3 Ckt Assignment 3 | E1 Inventory 3 Port 4 | E1 Inventory 3 Ckt Assignment 4 | E1 Inventory 3 Port 5 | E1 Inventory 3 Ckt Assignment 5 | E1 Inventory 3 Port 6 | E1 Inventory 3 Ckt Assignment 6 | FE Inventory 1 | FE Inventory 1 Port 1 | FE Inventory 1 NE Assignment 1 | FE Inventory 1 Port 2 | FE Inventory 1 NE Assignment 2 | FE Inventory 1 Port 3 | FE Inventory 1 NE Assignment 3 | FE Inventory 1 Port 4 | FE Inventory 1 NE Assignment 4 | FE Inventory 1 Port 5 | FE Inventory 1 NE Assignment 5 | FE Inventory 1 Port 6 | FE Inventory 1 NE Assignment 6 | FE Inventory 1 Port 7 | FE Inventory 1 NE Assignment 7 | FE Inventory 1 Port 8 | FE Inventory 1 NE Assignment 8 | FE Inventory 1 Port 9 | FE Inventory 1 NE Assignment 9 | FE Inventory 1 Port 10 | FE Inventory 1 NE Assignment 10 | FE Inventory 2 | FE Inventory 2 Port 1 | FE Inventory 2 NE Assignment 1 | FE Inventory 2 Port 2 | FE Inventory 2 NE Assignment 2 | FE Inventory 2 Port 3 | FE Inventory 2 NE Assignment 3 | FE Inventory 2 Port 4 | FE Inventory 2 NE Assignment 4 | FE Inventory 2 Port 5 | FE Inventory 2 NE Assignment 5 | FE Inventory 2 Port 6 | FE Inventory 2 NE Assignment 6 | FE Inventory 2 Port 7 | FE Inventory 2 NE Assignment 7 | FE Inventory 2 Port 8 | FE Inventory 2 NE Assignment 8 | FE Inventory 2 Port 9 | FE Inventory 2 NE Assignment 9 | FE Inventory 2 Port 10 | FE Inventory 2 NE Assignment 10 | ODF Inventory Port 1 | ODF Inventory Core Assignment 1 | ODF Inventory Core Distance Port 1 | ODF Inventory Port 2 | ODF Inventory Core Assignment 2 | ODF Inventory Core Distance Port 2 | ODF Inventory Port 3 | ODF Inventory Core Assignment 3 | ODF Inventory Core Distance Port 3 | ODF Inventory Port 4 | ODF Inventory Core Assignment 4 | ODF Inventory Core Distance Port 4 | ODF Inventory Port 5 | ODF Inventory Core Assignment 5 | ODF Inventory Core Distance Port 5 | ODF Inventory Port 6 | ODF Inventory Core Assignment 6 | ODF Inventory Core Distance Port 6 | ODF Inventory Port 7 | ODF Inventory Core Assignment 7 | ODF Inventory Core Distance Port 7 | ODF Inventory Port 8 | ODF Inventory Core Assignment 8 | ODF Inventory Core Distance Port 8 | ODF Inventory Port 9 | ODF Inventory Core Assignment 9 | ODF Inventory Core Distance Port 9 | ODF Inventory Port 10 | ODF Inventory Core Assignment 10 | ODF Inventory Core Distance Port 10 | Tx Overall Remarks | Rectifier 1 Brand | Rectifier 1 Voltage | Rectifier 1 Battery Current | Rectifier 1 Distribution Current | Rectifier 1 Rectifier Current | Rectifier 1 No. of RM | Rectifier 1 No. of Battery Bank | Rectifier 1 Battery Brand Bank 1 | Rectifier 1 Battery Bank 1 AH | Rectifier 1 Battery Brand Bank 2 | Rectifier 1 Battery Bank 2 AH | Rectifier 1 Battery Brand Bank 3 | Rectifier 1 Battery Bank 3 AH | Rectifier 1 Battery Brand Bank 4 | Rectifier 1 Battery Bank 4 AH | Rectifier 1 Battery Deformities | Rectifier 1 Battery Deformities Bank No | Rectifier 1 Battery Voltage Bank 1 | Rectifier 1 Battery Voltage Bank 2 | Rectifier 1 Battery Voltage Bank 3 | Rectifier 1 Battery Voltage Bank 4 | Rectifier 1 External Alarm Simulation | Rectifier 1 Breaker 1 Ampere Rating | Rectifier 1 Breaker 1 Load | Rectifier 1 Breaker 2 Ampere Rating | Rectifier 1 Breaker 2 Load | Rectifier 1 Breaker 3 Ampere Rating | Rectifier 1 Breaker 3 Load | Rectifier 1 Breaker 4 Ampere Rating | Rectifier 1 Breaker 4 Load | Rectifier 1 Breaker 5 Ampere Rating | Rectifier 1 Breaker 5 Load | Rectifier 1 Breaker 6 Ampere Rating | Rectifier 1 Breaker 6 Load | Rectifier 1 Breaker 7 Ampere Rating | Rectifier 1 Breaker 7 Load | Rectifier 1 Breaker 8 Ampere Rating | Rectifier 1 Breaker 8 Load | Rectifier 1 Breaker 9 Ampere Rating | Rectifier 1 Breaker 9 Load | Rectifier 1 Breaker 10 Ampere Rating | Rectifier 1 Breaker 10 Load | Rectifier 1 Breaker 11 Ampere Rating | Rectifier 1 Breaker 11 Load | Rectifier 1 Breaker 12 Ampere Rating | Rectifier 1 Breaker 12 Load | Rectifier 1 Breaker 13 Ampere Rating | Rectifier 1 Breaker 13 Load | Rectifier 1 Breaker 14 Ampere Rating | Rectifier 1 Breaker 14 Load | Rectifier 1 Breaker 15 Ampere Rating | Rectifier 1 Breaker 15 Load | Rectifier 1 Breaker 16 Ampere Rating | Rectifier 1 Breaker 16 Load | Rectifier 1 Breaker 17 Ampere Rating | Rectifier 1 Breaker 17 Load | Rectifier 1 Breaker 18 Ampere Rating | Rectifier 1 Breaker 18 Load | Rectifier 1 Breaker 19 Ampere Rating | Rectifier 1 Breaker 19 Load | Rectifier 1 Breaker 20 Ampere Rating | Rectifier 1 Breaker 20 Load | Rectifier 1 Breaker 21 Ampere Rating | Rectifier 1 Breaker 21 Load | Rectifier 1 Breaker 22 Ampere Rating | Rectifier 1 Breaker 22 Load | Rectifier 2 Brand | Rectifier 2 Voltage | Rectifier 2 Battery Current | Rectifier 2 Distribution Current | Rectifier 2 Rectifier Current | Rectifier 2 No. of RM | Rectifier 2 No. of Battery Bank | Rectifier 2 Battery Brand Bank 1 | Rectifier 2 Battery Bank 1 AH | Rectifier 2 Battery Brand Bank 2 | Rectifier 2 Battery Bank 2 AH | Rectifier 2 Battery Brand Bank 3 | Rectifier 2 Battery Bank 3 AH | Rectifier 2 Battery Brand Bank 4 | Rectifier 2 Battery Bank 4 AH | Rectifier 2 Battery Deformities | Rectifier 2 Battery Deformities Bank No | Rectifier 2 Battery Voltage Bank 1 | Rectifier 2 Battery Voltage Bank 2 | Rectifier 2 Battery Voltage Bank 3 | Rectifier 2 Battery Voltage Bank 4 | Rectifier 2 External Alarm Simulation | Rectifier 2 Breaker 1 Ampere Rating | Rectifier 2 Breaker 1 Load | Rectifier 2 Breaker 2 Ampere Rating | Rectifier 2 Breaker 2 Load | Rectifier 2 Breaker 3 Ampere Rating | Rectifier 2 Breaker 3 Load | Rectifier 2 Breaker 4 Ampere Rating | Rectifier 2 Breaker 4 Load | Rectifier 2 Breaker 5 Ampere Rating | Rectifier 2 Breaker 5 Load | Rectifier 2 Breaker 6 Ampere Rating | Rectifier 2 Breaker 6 Load | Rectifier 2 Breaker 7 Ampere Rating | Rectifier 2 Breaker 7 Load | Rectifier 2 Breaker 8 Ampere Rating | Rectifier 2 Breaker 8 Load | Rectifier 2 Breaker 9 Ampere Rating | Rectifier 2 Breaker 9 Load | Rectifier 2 Breaker 10 Ampere Rating | Rectifier 2 Breaker 10 Load | Rectifier 2 Breaker 11 Ampere Rating | Rectifier 2 Breaker 11 Load | Rectifier 2 Breaker 12 Ampere Rating | Rectifier 2 Breaker 12 Load | Rectifier 2 Breaker 13 Ampere Rating | Rectifier 2 Breaker 13 Load | Rectifier 2 Breaker 14 Ampere Rating | Rectifier 2 Breaker 14 Load | Rectifier 2 Breaker 15 Ampere Rating | Rectifier 2 Breaker 15 Load | Rectifier 2 Breaker 16 Ampere Rating | Rectifier 2 Breaker 16 Load | Rectifier 2 Breaker 17 Ampere Rating | Rectifier 2 Breaker 17 Load | Rectifier 2 Breaker 18 Ampere Rating | Rectifier 2 Breaker 18 Load | Rectifier 2 Breaker 19 Ampere Rating | Rectifier 2 Breaker 19 Load | Rectifier 2 Breaker 20 Ampere Rating | Rectifier 2 Breaker 20 Load | Rectifier 2 Breaker 21 Ampere Rating | Rectifier 2 Breaker 21 Load | Rectifier 2 Breaker 22 Ampere Rating | Rectifier 2 Breaker 22 Load | Rectifier 3 Brand | Rectifier 3 Voltage | Rectifier 3 Battery Current | Rectifier 3 Distribution Current | Rectifier 3 Rectifier Current | Rectifier 3 No. of RM | Rectifier 3 No. of Battery Bank | Rectifier 3 Battery Brand Bank 1 | Rectifier 3 Battery Bank 1 AH | Rectifier 3 Battery Brand Bank 2 | Rectifier 3 Battery Bank 2 AH | Rectifier 3 Battery Brand Bank 3 | Rectifier 3 Battery Bank 3 AH | Rectifier 3 Battery Brand Bank 4 | Rectifier 3 Battery Bank 4 AH | Rectifier 3 Battery Deformities | Rectifier 3 Battery Deformities Bank No | Rectifier 3 Battery Voltage Bank 1 | Rectifier 3 Battery Voltage Bank 2 | Rectifier 3 Battery Voltage Bank 3 | Rectifier 3 Battery Voltage Bank 4 | Rectifier 3 External Alarm Simulation | Rectifier 3 Breaker 1 Ampere Rating | Rectifier 3 Breaker 1 Load | Rectifier 3 Breaker 2 Ampere Rating | Rectifier 3 Breaker 2 Load | Rectifier 3 Breaker 3 Ampere Rating | Rectifier 3 Breaker 3 Load | Rectifier 3 Breaker 4 Ampere Rating | Rectifier 3 Breaker 4 Load | Rectifier 3 Breaker 5 Ampere Rating | Rectifier 3 Breaker 5 Load | Rectifier 3 Breaker 6 Ampere Rating | Rectifier 3 Breaker 6 Load | Rectifier 3 Breaker 7 Ampere Rating | Rectifier 3 Breaker 7 Load | Rectifier 3 Breaker 8 Ampere Rating | Rectifier 3 Breaker 8 Load | Rectifier 3 Breaker 9 Ampere Rating | Rectifier 3 Breaker 9 Load | Rectifier 3 Breaker 10 Ampere Rating | Rectifier 3 Breaker 10 Load | Rectifier 3 Breaker 11 Ampere Rating | Rectifier 3 Breaker 11 Load | Rectifier 3 Breaker 12 Ampere Rating | Rectifier 3 Breaker 12 Load | Rectifier 3 Breaker 13 Ampere Rating | Rectifier 3 Breaker 13 Load | Rectifier 3 Breaker 14 Ampere Rating | Rectifier 3 Breaker 14 Load | Rectifier 3 Breaker 15 Ampere Rating | Rectifier 3 Breaker 15 Load | Rectifier 3 Breaker 16 Ampere Rating | Rectifier 3 Breaker 16 Load | Rectifier 3 Breaker 17 Ampere Rating | Rectifier 3 Breaker 17 Load | Rectifier 3 Breaker 18 Ampere Rating | Rectifier 3 Breaker 18 Load | Rectifier 3 Breaker 19 Ampere Rating | Rectifier 3 Breaker 19 Load | Rectifier 3 Breaker 20 Ampere Rating | Rectifier 3 Breaker 20 Load | Rectifier 3 Breaker 21 Ampere Rating | Rectifier 3 Breaker 21 Load | Rectifier 3 Breaker 22 Ampere Rating | Rectifier 3 Breaker 22 Load | Main AC Breaker Rating | Main AC Load | AC Breaker 1 Rating | AC Breaker 1 Load | AC Breaker 2 Rating | AC Breaker 2 Load | AC Breaker 3 Rating | AC Breaker 3 Load | AC Breaker 4 Rating | AC Breaker 4 Load | AC Breaker 5 Rating | AC Breaker 5 Load | AC Breaker 6 Rating | AC Breaker 6 Load | AC Breaker 7 Rating | AC Breaker 7 Load | AC Breaker 8 Rating | AC Breaker 8 Load | AC Breaker 9 Rating | AC Breaker 9 Load | AC Breaker 10 Rating | AC Breaker 10 Load | AC Breaker 11 Rating | AC Breaker 11 Load | AC Breaker 12 Rating | AC Breaker 12 Load | AC Breaker 13 Rating | AC Breaker 13 Load | AC Breaker 14 Rating | AC Breaker 14 Load | AC Breaker 15 Rating | AC Breaker 15 Load | AC Breaker 16 Rating | AC Breaker 16 Load | AC Breaker 17 Rating | AC Breaker 17 Load | AC Breaker 18 Rating | AC Breaker 18 Load | AC Breaker 19 Rating | AC Breaker 19 Load | AC Breaker 20 Rating | AC Breaker 20 Load | Site Pictures | Site Log Book | Other Issues and Concerns | Supervisor | Date Signed | ARDS Item 1 | ARDS Quantity 1 | ARDS Details 1 | ARDS c/o 1 | ARDS Item 2 | ARDS Quantity 2 | ARDS Details 2 | ARDS c/o 2 | ARDS Item 3 | ARDS Quantity 3 | ARDS Details 3 | ARDS c/o 3 | ARDS Item 4 | ARDS Quantity 4 | ARDS Details 4 | ARDS c/o 4 | ARDS Item 5 | ARDS Quantity 5 | ARDS Details 5 | ARDS c/o 5 | ARDS Item 6 | ARDS Quantity 6 | ARDS Details 6 | ARDS c/o 6 | ARDS Item 7 | ARDS Quantity 7 | ARDS Details 7 | ARDS c/o 7 | ARDS Item 8 | ARDS Quantity 8 | ARDS Details 8 | ARDS c/o 8 | ARDS Item 9 | ARDS Quantity 9 | ARDS Details 9 | ARDS c/o 9 | ARDS Item 10 | ARDS Quantity 10 | ARDS Details 10 | ARDS c/o 10 | Deficiency Item 1 | Deficiency Description 1 | Deficiency Item No. 1 | Deficiency Item Brand 1 | Deficiency Item Model 1 | Deficiency Item Rating 1 | Deficiency Item Serial No. 1 | Deficeincy Item 2 | Deficiency Description 2 | Deficiency Item No. 2 | Deficiency Item Brand 2 | Deficiency Item Model 2 | Deficiency Item Rating 2 | Deficiency Item Serial No. 2 | Deficiency Item 3 | Deficiency Description 3 | Deficiency Item No. 3 | Deficiency Item Brand 3 | Deficiency Item Model 3 | Deficiency Item Rating 3 | Deficiency Item Serial No. 3 | Deficiency Item 4 | Deficiency Description 4 | Deficiency Item No. 4 | Deficiency Item Brand 4 | Deficiency Item Model 4 | Deficiency Item Rating 4 | Deficiency Item Serial No. 4 | Deficiency Item 5 | Deficiency Description 5 | Deficiency Item No. 5 | Deficiency Item Brand 5 | Deficiency Item Model 5 | Deficiency Item Rating 5 | Deficiency Item Serial No. 5 | Deficiency Item 6 | Deficiency Description 6 | Deficiency Item No. 6 | Deficiency Item Brand 6 | Deficiency Item Model 6 | Deficiency Item Rating 6 | Deficiency Item Serial No. 6 | Deficiency Item 7 | Deficiency Description 7 | Deficiency Item No. 7 | Deficiency Item Brand 7 | Deficiency Item Model 7 | Deficiency Item Rating 7 | Deficiency Item Serial No. 7 | Deficiency Item 8 | Deficiency Description 8 | Deficiency Item No. 8 | Deficiency Item Brand 8 | Deficiency Item Model 8 | Deficiency Item Rating 8 | Deficiency Item Serial No. 8 | Deficiency Item 9 | Deficiency Description 9 | Deficiency Item No. 9 | Deficiency Item Brand 9 | Deficiency Item Model 9 | Deficiency Item Rating 9 | Deficiency Item Serial No. 9 | Deficiency Item 10 | Deficiency Description 10 | Deficiency Item No. 10 | Deficiency Item Brand 10 | Deficiency Item Model 10 | Deficiency Item Rating 10 | Deficiency Item Serial No. 10 | Deficiency Item 11 | Deficiency Description 11 | Deficiency Item No. 11 | Deficiency Item Brand 11 | Deficiency Item Model 11 | Deficiency Item Rating 11 | Deficiency Item Serial No. 11 | Deficiency Item 12 | Deficiency Description 12 | Deficiency Item No. 12 | Deficiency Item Brand 12 | Deficiency Item Model 12 | Deficiency Item Rating 12 | Deficiency Item Serial No. 12 | Site Premise Remarks | Site Tower Remarks | Site Equipment(1) Remarks | Site Equipment(2) Remarks | Site BTS Equipment Remarks | Site Transmission Equipment Remarks | Site Genset and Day Tank Remarks | Site Deficiency Remarks
3326 Cabancalan.pdf | 3326 | Cabancalan | 2017-02-20 | Eric Brian Aligway | OK |  | N/A |  | Rectification | Line down conductor for rehab | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Rectification | PowerOne for Replacement | OK |  | OK |  | OK |  | Rectification | Genset power cable, with pending proj. Genset pad and shelter, Def. ATS | OK |  | OK | Line down conductor for rehab | OK |  | OK |  | OK |  |  | Off |  | Brgy. Cabancalan Mandaue | Intermmediate |  | Commercial Power | Indoor | 140ft. | Cabin Collapsible | 24/7 |  | Yes |  |  |  | 123.9206 | 10.3544 |  | Fluorescent bulb for replacment | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | For Rehab | OK | For Rehab | OK | OK | Expired | OK | Wo | OK | Ok | n/a | OK | OK | OK | Fire extinguisher for replacement | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KEDK15PC-0540048 | 51QSXRACCON19KEDN14PC-0568136 |  | Working | Working | Off | [5 empty] | Wo | None | None | Powercity | Defective | None | 45 | Working | CF100 |  | None |  | Working | None | 400li. |  | For CSMP Endo |  | Working | Genset no powercable with pending proj., def. battery, ATS def. fuel line for rehab |  | Retrieved |  | Retrieved |  | Retrieved |  | Off |  | Off |  | 3 | Off | None |  | Retrieved |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 3G MCSM | 2 | 2G MCSM | 3 | Bro EISM_244 electrical |  |  | 1 | FD LTE ECI FS AOC10 | [62 empty] | PowerOner | 54.3 |  |  | 37 | 2 | 2 | SacredSun | 180 | SacredSun | 180 |  |  |  |  | No | 1 | 47.8 | 47.9 |  |  | Off | [6 empty] | 63 | DCDU FD LTE |  |  | 40 | XDM100 A | [6 empty] | 10 | ECI FS A |  |  |  |  | 10 | BRO | 6 | CMM | 6 | FMS |  |  | 80 | bts3900 upper |  |  | 80 | bts3900 lower | [21 empty] | Off |  | 54 | 53.7 | 53.7 | 53.7 | Off | [18 empty] | 40 | XDM100 B | [6 empty] | 80 | DCDU 12B U2100/G1800 | [8 empty] | 16 | ECI FS B | [21 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
4222-Lahug 2-01092017.pdf | 4222 | Lahug 2 | 2017-01-09 | Lemuel Balbuena | OK |  | OK |  | Rectification | stolen | N/A |  | OK |  | Off |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A | mounting pole | OK |  | OK |  | OK |  |  | B |  | Aderan Hotel, Gorordo Avenue cor . Salinas Drive Ext., Brgy. Lahug, Cebu City | Commercial | Basement | Permanent | Building | Mounting pole | Room | 8am-5pm | Roving Guard | Yes |  |  |  | 123.8975 | 10.3313 |  | n/a | N/A | N/A | N/A | OK |  | Off | OK | Off | Off | OK | OK | OK | OK | OK | OK | working | OK | Ok | working | OK | OK | OK |  | WACU | Off | Off | Condura/WCONX019ED1 | Condura/WCONX019ED1 |  | 51QSXRACCONN19KEDT15PC-0704495 | 51QSXRACCONN19KEDR14PC-0592290 |  | Working | Working | Off | [6 empty] | Working | Off |  | None | None | n/a | None | Off | n/a | None |  | Off | None | n/a |  | Off | n/a | None |  | Huawei | Retrieved | Huawei | Retrieved | Huawei | Retrieved | Huawei | Retrieved | n/a | Off | Boser | 6 | Retrieved | Off | Huawei | Retrieved | Huawei | Retrieved |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | ECI FS/ECI XDM 100 | [38 empty] | ECI FS/ECI XDM100 | Port 1 | TD LTE | PORT 2 | ALLIED SWITCH | PORT 9 | BRO-ECI XDM100 | [14 empty] | ALLIED SWITCH | PORT 1 | 3G | PORT 2 | 2G | PORT 3 | FD LTE | PORT 21 | TRUNK TO ECI FS P2 | [12 empty] | PORT 1-2 | SALINAS |  | PORT 7-8 | BEVERLY | [26 empty] | Eltek 1 | 54.16 | 0 | 69 |  | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.9 | 53.9 | 53.9 | 53.9 | OK | 100 | FAILSAFE A | 100 | DCDU2 G1800 | 100 | DCDU1 L850 U2100 |  |  | 60 | 3G/LTE | 60 | 2G LOWER | [6 empty] | 40 | ECI B | 40 | TD LTE DCDU | [14 empty] | 16 | ECI APOLLO A | [6 empty] | ELTEK 2 | 54.03 |  | 9 |  | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 53.9 | 53.9 | 53.9 | 53.9 | OK | 100 | FAILSAFE B | 100 | 2G UPPER | [14 empty] | 40 | ECI A | [18 empty] | 16 | ECI APOLLO B | [19 empty] | Off | [5 empty] | Off | [44 empty] | 150 |  | 70 | ELTEK 2A | 70 | ELTEK 1A | 70 | ELTEK 2B | 70 | ELTEK 1B | [32 empty] | Done | OK |  |  |  | Battery | 4 banks |  | WFM | Huawei Cabinet | 1 |  | WFM | Eltek Old Rectifier | 1 | 61822000092 | WFM | Aircon | 1 | C08pc-0271684 | WFM
4305 Cabancalan WH.pdf | 4305 | Cabancalan WH | 2017-02-14 | Eric Brian Aligway | OK |  | N/A |  | Rectification | No Equipment and Van grounding | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | odu1 -32.9dbm odu2 -34.5 odu3 -34.3 | OK |  | OK |  | Rectification | No equipment grounding | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Percy Quijano | A | 2017-02-14 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
4394BASAK.pdf | 4394 | Basak | 2017-01-21 | Astrobal A. Trozo | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Rectification | waiting for IT for the installlation of Huawei software | Rectification | waiting for IT for the installlation of Huawei software | Rectification | for huawei rectification | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Rectification | for pldt rectification | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | defective ATS | OK |  | OK |  | Rectification | rusted roof | Off |  | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
4399-SOGOD-02082017.pdf | 4399 | Sogod | 2017-02-08 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | Off | GENSET PULLED-OUT | OK |  | OK |  | N/A | OUTDOOR | OK |  | OK |  |  | A |  |  | COMMERCIAL | LOT | PERMANENT | LOT | GUYED 80 FT | OUTDOOR | 24HRS | CARETAKER | Yes | [6 empty] | WORKING | OK | OK | OK | OK |  | Working | OK | OK | For Rehab | OK | OK | For Rectification | Off | None | Off | N/A | Off | Off | N/A | Off | Off | Off | OUTDOOR | Off | Off | Off | N/A |  |  | N/A |  |  | Off | Off | Off | [6 empty] | Off | Off |  | None | None |  | None | Off |  | None |  | None | Off |  |  | Off |  | None |  | HUAWEI | Retrieved |  | Off | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | HARRIES | STRATEX | Yes |  |  |  | OK | OK | Yes | CATMON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | ELTEK |  |  |  | 23 | 4 | 4 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | Off | [5 empty] | OK | [12 empty] | 40 |  | 40 | [5 empty] | 16 | [23 empty] | HUAWEI EPS |  |  |  |  | 4-not used |  | SACRED SUN | 150 | [6 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 16.9 |  |  | 70 | ELTEK 1 |  |  | 70 | ELTEK 2 | [32 empty] | Done | OK |  |  |  | CABINET | 1 | HUAWEI |  | BATTERY | 2 BANKS | ACME
5816ImperialPalace1-.pdf | 5816 | Imperial Palace 1 & 2 | 2017-02-08 | Eddie D. Clave Jr. | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | excess mats for ARDA | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | For additional rectifier | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | excess mats for pull-out/ARDA | Rectification | excess mats for ARDA | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
5835 Ma Luisa meow.pdf | 5835 | Ma. Luisa Meow | 2017-02-06 | Eric Brian Aligway | OK |  | OK |  | N/A | For Grounding installation | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | -64.4dbm, meow for relocation | OK |  | OK |  | N/A |  | Rectification | Need cable ladder | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK | Need additional 2 banks battery | N/A |  | OK | Temporary tap to guard hause | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
5840-CEBU NORTH RECLAIMATION-01312017.pdf | 5840 | CEBU NORTH RECLAIMATION | 2017-01-31 | LEMUEL BALBUENA | OK |  | OK |  | Rectification | STOLEN OUTSIDE GROUNDING | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | ROOFTOP | PERMANENT | BUILDING | BIPOD 30FT | VAN | 8AM-5PM | ROVING GUARD,ADMIN/BLDG SECURITY | Yes | [6 empty] | N/A | N/A | N/A | N/A | Off |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | WORKING | OK | Ok | WORKING | OK | OK | OK |  | Off | WACU | Off | CONDURA | CONDURA |  | B15PC-0141452 | J16PC-0975026 |  | Working | Working | Off | 8 | 8.2 |  |  |  | N/A | Working | Off | N/A | None | None | N/A | None | Off | N/A | None | N/A | None | Off | N/A | N/A | Off | N/A | None |  | HUAWEI | Retrieved | HUAWEI | Off | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Yes | 14935/14963/14991 | 14515/14543/14571 | 33.3/34.6/30.8 | OK | OK | Yes | CDU |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | HUAWEI | NE40E | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | ZTE | 53.3 |  | 74.7 |  | 3 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 50.5 | 50 | 49.8 |  | OK | 100 | G1800 DCDU POWER | 100 | U2100/G900 DCDU POWER | [8 empty] | 50 |  |  |  | 32 | HUAWEI CEN PH3 POWER A |  |  | 80 | HUAWEI BTS3900 UPPER |  |  | 80 | L850 DCDU POWER | 40 | HUAWEI CEN PH3 POWER B |  |  | 16 | RTN950 FACING CDU | [12 empty] | ELTEK | 53.97 | 12 | 7 |  |  |  | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 52.2 | 52.2 | 52.2 | 52.2 | OK | [16 empty] | 63 | BTS3900 LOWER | [10 empty] | 40 | HUAWEI CEN B | [6 empty] | 16 | RTN950 MAIN CDU | [21 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 30.8 | 70 | ZTE RECTIFIER | 70 | ELTEK 1 | 32 | AIRCON 1 | 32 | AIRCON 2 | 32 | SPARE | 32 | ELTEK 2 | 20 | LIGHTING | 20 | C.O | 20 | TOWER LIGHT | 20 | PERIMETER | [20 empty] | Done | OK |  |  |  | AIRCON | 1 | CONDURA/K10PC-0466444 | WFM | CABINET BTS3900 | 1 | HUAWEI/21021131696TBA902293 Y WD2B5MID | WFM
5866 Bigfoot Checklist.pdf | 5866 | Mactan Bigfoot | 2017-03-09 | Eddie D. Clave Jr. | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Rectification | 1 RM missing on eltek; defective powerone display | OK |  | N/A |  | OK |  | Rectification | defective genset | OK |  | OK |  | Rectification | 2 wacu defective high temp on site | Rectification | excess mats for pull-out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
5888-Cebu Parklane Hotel-02062017.pdf | 5888 | Parklane International Hotel | 2017-02-06 | Lemuel Balbuena | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | Empower Rectifier for replacement | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK | pole | OK |  | OK |  | OK |  |  | Off |  |  | Commercial | 5th Floor Building | Permanent | Building | Pole | Van | 8am-5pm | Roving Guard, Admin/Bldg Security | Yes | [6 empty] | n/a | N/A | N/A | N/A | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | OK | OK | 2000-02-01 | OK | Ok | working | OK | OK | Off |  | WACU | WACU | Off | CONDURA | CONDURA |  | J16PC-'0975032 | K15PC-'0540066 |  | Working | Working | Off | 8 | 8 |  | QHL6001 |  | N/A | Working | Off | N/A | None | None | N/A | None | Off |  | None |  | Off | Off |  |  | Off |  | Off |  | HUAWEI | Retrieved |  | Off | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | MABOLO |  | 1 | CEN | 2 | CEN | [35 empty] | LA4 | 3G | [70 empty] | ELTEK | 54.19 |  | 16 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.3 | 53.2 | 53.1 | 53.1 | Off | 100 | DCDU | [40 empty] | 16 | CEN DCPDB ATN 950B (B) | EMPOWER | 54.64 | 3.4 | 25 |  | 3 | 1 | POWERSAFE | 155 | [6 empty] | No | [5 empty] | Off | 40 | BTS3900 | [8 empty] | 16 | CEN DCPDB ATN 950B (A) | [8 empty] | 80 | HUAWEI BTS 3900 UPPER | 80 | HUAWEI BTS 3900 LOWER | [35 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 16 | 70 | Empower | 70 | Eltek A | 50 |  | 50 | Eltek B | 40 |  | 40 |  | 40 |  | 40 |  | 30 |  | 30 | ACU 1 | 30 |  | 30 | ACU 2 | 20 | LIGHTS | 20 | [13 empty] | Done | OK |  |  |  | AIRCON | 2 | CONDURA/H10PC-0380073-CARRIER/J08PC-'0519783 | WFM | BATTERY | 3 BANKS | LYNX/170 | WF,
768 Punta Engano.pdf | 768 | Punta Engano | 2017-01-09 | EDDIE CLAVE JR | OK | all vswr passed. record on text file | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Off |  | Rectification | for replacement of other labels | OK | 17Q10027- with mains c/o NCC-VIS Lau | Rectification | for busbar fixation | OK |  | OK |  | N/A | bypass due to high crc it contributes | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | 2 Powerone RM for replacement | Off |  | N/A | no tvss and surge protection | Off |  | Rectification | Prime site. 2 genset and 1 genset defective | N/A |  | OK | Cannot accomodate additional tower loading | Rectification | Port holes for resealant | OK |  | OK |  |  | B | 2017-01-09
802 Comspostela PMR.pdf | 802 | Compostela | 2017-01-27 | Greggy Vale/Albert Ambil | OK | All are 1.1. | N/A | NOT APPLICABLE | Rectification | OUTDOOR GROUNDING FOR REHAB SINCE SOME ARE STOLEN. | N/A | NOT APPLICABLE | N/A | NOT APPLICABLE | OK |  | OK | NOT APPLICABLE | OK | ok. | OK | Done for all 3 MW antennas. Old Nokia MW antenna, recovered during PMR. | N/A |  | OK | ok. | OK | Done for 3G, no LTE yet during PMR. | Rectification | 1. 802 facing W74 CompostelaTP: -46dBm/-52dBm 2. 802 facing 804Liloan: -40/-44dBm and -47dBm/-48dBm | OK | ok done. | OK | ok done. | OK | ok. | OK | ok | OK | ok. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | Off | OK. | OK | OK DONE. | OK | OK DONE. | OK | OK. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK | 1 DEFECTIVE NOKIA RM. VOLTAGE: -54.5V. DONE | OK | OK DONE. MORE THAN 3 HOURS BACK-UP. | N/A | NOT APPLICABLE. | OK | OK. | OK | ATS FUSE DEFECTIVE. GENSET OK. | OK | ok commercial power. | OK | OUTDOOR VAN BUSBAR STOLEN | OK |  | Rectification | Need grasscutting. | OK |  | Percival Quijano | A | 42762 | Brgy. Estaca, Compostela, Cebu | RESIDENTIAL | LOT | PERMANENT | LOT | GUYED 32m | VAN COLLAPSIBLE | 24 HOURS | CARETAKER | Yes | 2017 | UNKNOWN | NA | 10.4402 | 124.0089 | Brgy. Estaca, Compostela, Cebu | 5, 0 | OK | OK | for Replacement | For CSMP Endo | 2 PADLOCK FOR REPLACEMENT | Defective | Off | OK | OK | OK | OK | For Rectification | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | WACU | WACU | Off | WCONR019ED | WCONX019ED1 |  | 141701632 | 51QSXRACCON19KEDF15PC-0355090 |  | Defective | Working | None | FOR ARDA | 8 | NOT APPLICABLE | NONE | NONE | 1, 0 | None | None | DENYO SN: 5391801 | Defective | None | 25 | None | CF100 | 1957 | None | 5385-C | Defective | None | 100 | 90233309 | Working | 0 | Working | ATS KUTAI DEFECTIVE SN: 8301 | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900L | Off | BTS3900L | Retrieved | NONE | Off | NONE | NONE | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | AVIAT | AVIAT | Yes |  |  | 0.88889 | OK | OK | Yes |  | AVIAT | AVIAT | Yes |  |  | 0.95833 | OK | OK | Yes |  | HUAWEI | RTN950 | Yes |  |  | -35 | OK | OK | Yes |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | APOLLO | Yes | Trad | Yes | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  |  |  | NONE | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | HUAWEI RTN950 EG4 FACING W74 | 1 | 802/W74 PABIS AGGREGATE (FROM S6 P3 FACING LILOAN) | 2 | W74 COMPOSTELA 2G PABIS (TO GTMU) | 3 | W74 COMPOSTELATP 3G (FROM PORT 4)ALLIED) | [14 empty] | ALLIED SWITCH | 1 | VACANT | 2 | VACANT | 3 | 802 COMPOSTELA 3G (TO UMPTb1) | 4 | W74 COMPOSTELATP 3G (TO EG4 PORT 3) | 20 | AGGREGATE PORT TO ECI FS u0/2 | [10 empty] | 42737 | FACING LILOAN | FOR CHECKING | 42798 | FACING DANAOTP | FOR CHECKING | [25 empty] | ELTEK | 54.01V | 0 | 30 A | 30 A | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No | NA | 53.9 V | 53.8V | 53.9V | 53.8V | OK | 100 | DCDU U2100 | 100 | VACANT | 100 | VACANT | 100 | VACANT | 63 | DCDU 12B RTN | 63 | VACANT | 63 | VACANT | 63 | VACANT | 63 | VACANT | 40 | VACANT | 40 | VACANT | 40 | VACANT | 40 | VACANT | 40 | VACANT | 40 | DCDI 03C 850 | 20 | HARRIS B | 20 | ECI APOLLO B | 20 | VACANT | 16 | VACANT | 16 | RTN950 REDUNDANT | 16 | VACANT | 16 | ALLIED TURBO SWITCH | NOKIA | PSS | 0 | 25.9 A | 25.9 A | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No | NA | 53.5 V | 53.9 V |  |  | OK | 32 | VACANT | 32 | VACANT | 32 | VACANT | 32 | VACANT | 32 | VACANT | 32 | VACANT | 16 | RTN950 POWER MAIN | 16 | VACANT | 16 | HARRIS A | 16 | ECI RAP 4B SOURCE A | 80 | BTS3900L UPPER | [22 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 40 | BTS1800 CABINET PSSS RECTIFIER | 30 | ELTEK 1 | 30 | VACANT | 30 | C.O. | 30 | ELTEK 2 | 20 | C.O. | 30 | ACU2 | 20 | C.O. | 100 | FROM ECB | 20 | LIGHTING | [20 empty] | Done | OK |  | PERCIVAL QUIJANO | 42762 | [40 empty] | SUPPORT | ATS | 1 | KUTAI | KUTAI |  | SN: 8301 | SUPPORT | OUTDOOR BUSBAR | 1 | NONE | NONE |  | NOT APPLICABLE | [71 empty] | As seen on the photo, on going recovery of old Nokia MW radio.
804 Liloan.pdf | 804 | Liloan Calero | 2017-02-10 | G. Vale/A.Ambil | OK | For 3G VSWR: 1.1 all. For LTE FD: 1.1 to 1.4. For LTE TD: 1.1 to 1.2. | N/A |  | Rectification | stolen bus bar and grounding. | N/A | NOT APPLICABLE. | OK |  | OK |  | OK |  | OK |  | Rectification | Low rsl 804liloan facing 802 compostela, to follow antenna panning. | OK |  | OK |  | OK | Done for 3G/LTE FD and TD. | OK | -42dBm for 804 facing 802. The rest -33dBm to -36dBm. | OK |  | OK |  | Rectification | Stolen grounding, already reported security. | OK |  | OK |  | N/A | Bypassed. Not used. | OK | ok. | OK |  | OK |  | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK |  | OK |  | Rectification | Eltek #2 battery for replacement. | OK |  | OK |  | OK |  | OK |  | OK | stolen bus bar/grounding | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 42776 | Brgy. Calero, Liloan Cebu | Residential | Lot | Permanent | Lot | SST 50m | Van | 24 Hours | Caretaker | Yes | 2018 | Marina Jalang Cagang | 9183225287 | 123.9961 | 10.3681 | Brgy. Calero, Liloan Cebu | 2, 4 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | 1, 3 | OK | For Rehab | none | OK | OK | For CSMP Endo |  | WACU | WACU | WACU | WCONX019ED1 | WCONX019ED1 | WCONX019ED1 | 51QSXRACCON19KEDJ13PC-0317928 | 51QSXRACCON19KEDJ16PC-0975030 | 51QSXRACCON19KED | Working | Working | Defective | 7.8 | 8.2 | NOT INSTALLED/DEFECTIVE | ASAHI | ASAHI | 1, 0 | Defective | Defective | DENYO SN: 3719820 | Working | Working | 45 | Working | CF200 | 1190 | Working | MTR1086095 | Working | None | 100L | 14755685 | Working | 0 | Working | ATS POWERCITY SN: 15030779 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | DECOM | Off | IBM | 6 | Retrieved | None | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off |  | OK | OK | HUAWEI | RTN980 | Yes |  |  | -36dBm | OK | OK | Yes | 4393 AYALA HEIGHTS | HUAWEI | RTN950 | Yes | 14935/14991/1493 |  | -33dBm | OK | OK | Yes | V3498 Sun Calero | AVIAT | HSTX | Yes | 7625 | 7457 | -42dBm | OK | OK | Yes | 802 Compostela | AVIAT | HSTX | Off | N/A | N/A | N/A | OK | Off | Off | 4393 AYALA HEIGHTS FOR DECOM | Fujitsu | FRX | Yes | VIA NMS | VIA NMS | -39dBm | OK | OK | Yes | 816 MSC3 and 805 Danao | none |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | XDM-100 | Yes | Trad | Yes | ECI | APOLLO | Yes | Trad | Yes | NONE | NONE | Off | Off | Off |  | AVIAT FACING 4394 AYALA HEIGHTS | S7- P3 | ADLAON 2G 1ST E1 | S7- P4 | ADLAON 2G 2ND E1 | S7-P5 | TV5 1ST E1 | S7-P6 | TV5 2ND E1 | S7-P9 | LUSARAN 2G 2ND E1 | S7-P10 | LUSARAN 2G 3RD E1 | AVIAT FACING 802 COMPOSTELA | S7-P11 | W74 WIMAX 1ST E1 | S7-P12 | W74 WIMAX 2ND E1 | S7-P13 | W74 WIMAX 3RD E1 | S7-P14 | W74 WIMAX 4TH E1 |  |  |  |  | ALLIED SWITCH FE PORTS | 2 | RTN NMS | 3 | 804 LILOAN LTE FD | 5 | V3498 SUN CALERO 2G PABIS | 6 | 804 LILOAN 2G PABIS | 7 AND 8 | P7: V3498 SUN CALERO 3, P8: 804 Liloan 3G | 11 | AYALA HEIGHTS 3G CLUSTER | AVIAT FACING 802 COMPOSTELA | S6-P3 | W74/802 PABIS AGGREGATE (TO RTN980 EG4 P2) | [6 empty] | ECI FS | ECI FS APOLLO | u0/2 | 804 LILOAN LTE TD |  |  | ECI XDM-100 |  | i5-14 | 804 Liloan calero BRO |  |  | EG4 RTN980 FACING AYALA HEIGHTS | S1-P1 | PABIS AGGREGATE (TO ECI i5-P16) | S1-P2 | PABIS W74/802 (TO FACING 802 HSTX S6-P3) | S1-P3 | FOR VERFICATION | S1-P4 | AYALA HEIGHTS 3G CLUSTER | [43 empty] | ELTEK | 53.01 V | 0 | 35 | 35 | 4 | 4 | LYNX | 170 | LYNX | 170 | LYNX | 170 | LYNX | 170 | Off |  | 47 | 46 | 47 | 47.3 | For Rectification | 100 | DCDU U2100B | 100 | DCDU L850 | 100 | FOR VERIFICATION | 100 | FOR VERIFICATION | 63 | SPARE | 63 | FOR VERIFICATION | 63 | FOR VERIFICATION | 63 | 2G LOWER | 63 | 2G UPPER | 40 | FOR VERIFICATION | 40 | FUJITSU A FACING MSC3 | 40 | ALCATEL | 40 | RTN980 FACING AYALA HEIGHTS MAIN | 40 | FOR VERIFICATION | 40 | FOR VERIFICATION | 20 | FMS | 20 | SPARE | 20 | SPARE | 16 | ALLIED SWITCH TURBO | 16 | RTN950 FACING SUN CALERO MAIN | 16 | SPARE | 16 | SPARE | ELTEK | 54.29 V | 0 | 70 | 70 | 4 | 4 | LYNX | 170 | LYNX | 170 | LYNX | 170 | LYNX | 170 | Off |  | 50.1 | 51 | 49.9 | 50.1 | OK | 100 | VAPEL B | 100 | FOR VERIFICATION | 100 | FOR VERIFICATION | 100 | SPARE | 63 | SPARE | 63 | LTE TDD | 63 | SPARE | 63 | SPARE | 63 | FOR VERIFICATION | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | DCPDB B HARRIS | 40 | FOR VERIFICATION | 40 | RTN980 FACING AYALA REDUNDANT | 20 | FMS | 20 | SPARE | 20 | SPARE | 16 | ECI APOLLO B | 16 | RTN950 FACING SUN LILOAN CALERO | 16 | SPARE | 16 | SPARE | ELTEK OLD | [14 empty] | Off | [5 empty] | Off | 50 | NFRX DCPDB | 50 | FUJITSU DCPDB B | 32 | FOR VERIFICATION | 32 | HARRIS DCPDB MAIN | 32 | FUJITSU DCP A | 32 | ECI XDM-100 SOURCE B | 32 | ECI XDM-100 SDH SOURCE A | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | ECI APOLLO SOURCE A | 10 | ROUTER IBM | 10 | TELLABS 8620 POWER A | 10 | SPARE | 10 | SPARE | 6 | SPARE | 6 | SPARE | 6 | SPARE | 100 | 100 | 70 | ELTEK OLD | 70 | ELTEK 2 | 70 | ELTEK 1 | 30 | FOR VERIFICATION | 30 | ACU | 30 | DACO/ECB | 20 | SPARE | 20 | LIGHT | 20 | EXHAUST FAN | 70 | ELTEK 1 | 30 | SPARE | 70 | ELTEK 2 | [16 empty] | Done | OK |  | PERCIVAL QUIJANO | 42776 | [40 empty] | SUPPORT | VAN LIGHTS | 1 | N/A | NA | NA | NA | SUPPORT | DEF. RECT. BATTERIES |  | LYNX |  | 170AH | FOR ELTEK 1 AND 2
813_San_Remigio_030717.pdf | 853 | SAN REMIGIO | 2017-03-07 | Jerome T. Butong / Albert Ambil | N/A |  | N/A |  | N/A | No indoor and outdoor busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK | MSN not readable | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | no installed busbar inside and outside the equipment room | OK |  | OK |  | OK | Installed surge suppressor for Microwave radio only | N/A | only one extended AP | OK |  | OK |  | N/A |  | N/A | no ODF | N/A |  | N/A |  | N/A |  | OK | for additional battery both Eltek and Emerson( sacred sun 180 Ah | OK | 1 bank battery voltage reading 53.6 V(eltek) and 54.2 V at Emerson rectifier (1 bank) | OK |  | OK |  | N/A | no genset | OK |  | OK |  | Rectification | Only one WACU installed since after Yolanda | Rectification | Excess material from RTN950 microwave installation still on site; | OK |  | Percival B. Quijano | B | 42800 | Poblacion, San Remigio, Cebu | Residential | Lot | Permanent | Lot | SST / 150 Ft | Concrete | 24 hours | Caretaker | Yes | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | N/A | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | For Rectification | OK | None | OK | 2 working / 2 not working | OK | Ok | no emergency light | OK | For Rectification | For CSMP Endo | Excess materials still on site | WACU | WACU | Off | WCONA019ED |  |  | 51QSXRACCON19KED |  |  | Working | None | None | 1.02 | [5 empty] | None | None |  | Working | None |  | None | CF200 |  | None | 68724 | None | None |  | TO FOLLOW | For CSMP Endo | none | Working | Site AC loading: 9.83 A |  | Off |  | Off | BTS3900 | Retrieved |  | Off |  | Off | Extended AP | 1 | Retrieved | Off |  | Off |  | Off |  | Off | 3G: U2100; | OK | OK | HUAWEI | RTN950 | No | 8088.67 / 8147.97 | 7777.35 / 7836.65 | 0.9891 | OK | Off | Yes | 813 Bogo | AVIAT |  | Yes | 7457 | 7625 | 1.0026 | OK | OK | Yes | 813 Bogo |  |  | No |  |  |  | Off | Off | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | Off |  |  |  | Off |  | Off | NA | [14 empty] | Yes | Off | Yes |  |  | Yes | Off | Yes |  |  | Yes | Off | No | [40 empty] | AVIAT facing Bogo | S3-P1 | 813 San Remigio BRO Extended AP | S3-P2 | 813 San Remigio 3G | [68 empty] | ELTEK | 53.80 V | 0 | 0.041667 | 0.041667 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No | 1 | 53.7 V | 53.7 V | 53.7 V | 53.7 V | For Rectification | 100 |  | 100 |  | 100 |  | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 | DCPDB B | 20 |  | 20 |  | 16 | HUAWEI RTN950 RDNT FACING 813 BOGO | 16 |  | 16 |  | 16 |  | EMERSON | 54.6 V | 0 | 18.3 A | 18.3 A | 6 | 2 | SACRED SUN | 100 | SACRED SUN | 100 |  |  |  |  | No |  | 54.4 V | 54.4 |  |  | OK | 100 | BATTERY 1 | 100 | BATTERY 2 | 100 |  | 100 |  | 16 |  | 16 | DCPDB A | 16 | HUAWEI RTN950 MAIN FACING 813 BOGO | 16 |  | 6 |  | 6 |  | 6 |  | 6 |  | 63 | 3G DCDU | 63 |  | 63 |  | 63 |  | 32 |  | 32 |  | 32 |  | 32 | [20 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 100 | EMERSON | 40 |  | 70 | ACU 1 | 30 | ACU 2 | 30 | ELTEK 1 | 30 | ACU 3 | 70 | ELTEK 2 | 20 | C. O. | 20 |  | 20 | LIGHTING | [20 empty] | Done | OK |  | PERCIVAL B. QUIJANO | 42801
818 Marigondon Checklist.pdf | 818 | Marigondon | 2017-03-01 | Eddie D. Clave Jr. | OK | for 2g & 3g all vswr passed <1.2 for LTE all vswr passed <1.3 | OK |  | Rectification | Stolen tower grounding busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For re-labeling | Rectification | For cabling of external alarms via Emerson(refarm); Missing controller for Eltek | Rectification | stolen tower grounding busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | missing eltek controller(smartpack); for replacement of emerson rectifier; for replacement of 4 banks 100AH Narada | Off |  | Rectification | TVSS OB light no light for checking | OK |  | Rectification | genset fuel leak when operating for CSMP checking | OK |  | Rectification | stolen grounding busbar on tower | Rectification | for roofing rehab; excess mats on site for pull-out; porthole for sealanat | Rectification | for grass uprooting and clean-up | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
825Lapulapu.pdf | 825 | Lapu-lapu | 2017-02-18 | Astrobal A. Trozo | OK |  | N/A | no diplexers, trixplexers and combiners | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | waiting for IT for huawei software installation | N/A | waiting for IT for huawei software installation | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | manually operated since battery is defective | OK |  | OK |  | Rectification | broken wall | Rectification | major grass cutting ; excess materials for pull out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
827 MEPZ Checklist.pdf | 827 | MEPZ | 2017-03-20 | Eddie D. Clave Jr. | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Off |  | OK |  | OK |  | OK |  | OK |  | N/A | bypass surge supressor due to high CRC | OK |  | OK |  | OK |  | OK |  | Rectification | for regrooming by PLDT | N/A |  | N/A |  | N/A |  | OK |  | OK |  | Rectification | no protection; defective TVSS | OK |  | Rectification | Defective genset/ATS. For CSMP checking | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | excess mats for pull-out; need grass cutting | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
845 Mactan Shangrila Checklist.pdf | 845 | Mactan Shangrila | 2017-02-13 | Eddie D. Clave Jr. | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | Rectification | For relabeling | Rectification | excess mats for pull-out c/o Huawei | OK |  | OK |  | OK |  | N/A | bypass due to high CRC | OK |  | OK |  | N/A |  | OK |  | Rectification | For regrooming c/o PDT | N/A |  | N/A |  | OK |  | Rectification | 4 banks lynx for replacement | OK |  | OK |  | OK |  | Rectification | defective ATS | N/A |  | OK |  | Rectification | port hole for sealant | OK |  | OK |  |  | B | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
847 Basak Mandaue.pdf | 847 | Basak Mandaue | 2017-02-09 | A. Ambil | OK | All are 1.1 to 1.2 for 3G. for LTE with VSWR 1.9 already endorsed to Huawei due to refarm projects. | N/A | NOT APPLICABLE. | OK |  | N/A | NOT APPLICABLE. | OK |  | OK |  | OK |  | OK |  | N/A | NOT APPLICABLE. | OK |  | OK |  | OK | DONE FOR 3G/LTE FD. | N/A | NOT APPLICABLE. | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | NOT APPLICABLE. | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | Rectification | NEED ADDITIONAL RM FOR OLD ELTEK. | OK | 30 MINUTES ONLY | OK | ok | Off |  | Rectification | DEFECTIVE ATS. | OK |  | OK |  | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 42775 | Brgy. Basak, Mandaue City | Commercial | Lot | Permanent | Lot | Guyed 32m | Van | 24 hours | Caretaker | Yes | 2017 | unknown | unknown | 123.9511 | 10.3645 | unknown | 4, 0 | OK | for CSMP Endo | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | Off | OK | OK | 2, 2 | OK | Ok | none | OK | OK | OK |  | WACU | WACU | WACU | WCONX019ED1 | WCONX019ED1 | WCONX019ED1 | 51QSXRACCON19KED T15PC-0704442 | 51QSXRACCON19KED J13PC-0317926 | 51QSXRACCON19KED J16PC-0963266 | Working | Working | Working | 8 | 8.3 | 8.4 | ASAHI | ASAHI | 1, 0 | Working | Working | DENYO SN: 5394548 | Defective | Working | 25 | Working | CF100 | 726 | None | VECO 0263 EGS0 | Working | None | 15 INCHES | 10672397 | Working | NONE | Working | ATS BRAND: KUTAI, SN: 8313 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | BOSER | 6 | Retrieved | None | BTS3900 | Retrieved | NONE | Off | NONE | Off |  | OK | OK | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | XDM-100 | Yes | Trad | Yes | ZTE | ZXMP M721 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  |  | NONE | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | ECI XDM-100 | i5-9 | 847 Basak IBM router | i5-16 | 847 Basak 2G | [16 empty] | OPTICAL ZTE FS | SLOT 10 C1 | 847 BASAK 3G | SLOT 9 C1 | 847 BASAK LTE FD | [16 empty] | A 1/2 | FACING LABOGON | 2.699 km | B 1/2 | FACING CONSOLACION2 | 2.4211 km | [25 empty] | ELTEK | 54.63 V | 0 | 78 A | 78 A | 4 | 2 | LYNX | 170 AH | LYNX | 170 AH | NONE |  | NONE |  | No |  | 53.8 | 53.5 | NONE | NONE | OK | 100 | ZTE PDU/VAPEL B | 100 | DCDU | 100 | DCDU | 100 | DCDU1 | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | BTS3900 LOWER | 63 | BTS3900 UPEER | 40 | ECI A | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | ZTE FS REDUNDANT | 20 | SPARE | 20 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | ELTEK OLD | 54.0 V | 0.041667 | 0 | 0 | 2 | 2 | LYNX | 170AH | LYNX | 170AH | NONE |  | NONE |  | No |  | 53.4 | 53.4 | NONE | NONE | OK | 100 | ZTE PDU MAIN | 100 | SPARE | 50 | SPARE | 50 | SPARE | 32 | SPARE | 32 | SPARE | 32 | ZTE FS MAIN | 32 | LTE DCDU POWER | 32 | ECI B | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 10 | IBM | 10 | SPARE | 10 | SPARE | 10 | SPARE | 6 | 25. RRU0 | 6 | 26. RRU1 | 6 | 27. RRU2 | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 40 | ELTEK OLD | 40 | SPARE | 30 | ACU2 | 30 | ACU1 | 30 | CO | 30 | ACU3 | 20 | OUTLET | 20 | LIGHTING | 70 | ELTEK NEW | 20 | DTS SUPPLY | [20 empty] | Done | OK |  | PERCIVAL QUIJANO | 42775 | SUPPORT | 1 | NOKIA EMPOWER SN: 2355444 | WFM | SUPPORT | 1 | NOKIA EMPOWER SN: UNREADABLE | WFM | [32 empty] | SUPPORT | ATS | 1 | KUTAI |  |  | SN: 8313
848-NAWANAO-02112017.pdf | 848 | NAWANAO | 2017-02-11 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | ROUTER IN MSC3 | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | B |  |  | COMMERCIAL | ROOFTOP | PERMANENT | BUILDING | GUYED 80 FT | VAN | 8AM-5PM | ROVING GUARD | Yes | [6 empty] | N/A | Off | N/A | Off | Off | BUILDING SITE | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-05-01 | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | CONDURA | CARRIER |  | B13PC-'061423 | 111614438 |  | Working | Defective | Off | 8.7 | DEFECTIVE COMPRESSOR |  |  |  |  | Defective | Off |  | None | Off |  | None | Off |  | None |  | Off | Off |  |  | Off |  | Off | INHOUSE A1 | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | ZTE | retrieved | IBM | 6 | Retrieved | None | HUAWEI | Retrieved |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  | 35.1/35.1/36.1 | OK | OK | Yes | PARKMALL | HUAWEI | RTN950 | Yes | 14529/14587/14645 | 14949/15007/15065 | 33.9/32.9/31.4 | OK | OK | Yes | CASALS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM100 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | ELTEK | 54.001 |  |  | 71 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 52.2 | 51.9 | 51.5 | 51.1 | Off | 100 | Refarming breaker u2100 and GU900 | 100 | Refarming breaker G1800 | 100 | HUAWEI BTS 3900L -48 UPPER |  |  | 63 | HUAWEI BTS 3900L -48 LOWER | 63 | FD LTE DCDU | [18 empty] | 20 | RTN Redundant Main 1 facing V3478 |  |  |  |  | 16 | RTN 950 Main facing ParkMall |  |  |  |  | 16 | XDM100B | ELTEK OLD | 54.1 |  |  | 33 | 5 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 33.2 | 40 | ELTEK 2 | 70 | ELTEK OLD | 30 | C.O | 30 | ACU 2 | 30 | ACU 1 | 63 | ZTE | 20 | LIGHTS | 20 | SPARE | 20 | SPARE | 60 | ELTEK | [20 empty] | Done | OK
849 Plantation Bay Checklist.pdf | 849 | Plantation Bay | 2017-02-14 | Astrobal A. Trozo | OK | all passed | OK |  | Rectification | stolen grounding busbar | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | facing Marigondon2 ISV3-3=-34dBm(TX:14599 RX:15019) ISV3-4= -33.3dBm(TX:14655 RX:15075) ISV3-5=-33.4dBm(TX:14515 RX:14935) facing Subabasbas ISV3-3=-34.7dBm(TX:14543 RX:14963) ISV3-4=-33,4dBm(TX:14571 RX:14991) ISV3-5=-34.6dBm(TX:14657 RX:15077) | Rectification | for relabelling | OK |  | Rectification | stolen grounding busbar | OK |  | OK |  | N/A | bypass due to high CRC | OK |  | OK |  | OK |  | OK |  | Rectification | for regrooming c/o PLDT | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK | defective ATS; prime site | N/A |  | OK |  | Rectification | excess mats for pull-out | Rectification | for grasscut and cleaning | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
854 TABOGON-03222017.pdf | 854 | TABOGON | 2017-03-22 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | MANUAL GENSET | OK |  | OK |  | OK |  | OK |  | OK |  |  | B |  |  | COMMERCIAL | LOT | PERMANENT | LOT | SST 150FT | CONCRETE ROOM | 24HRS | CARETAKER | Off | [6 empty] | WORKING | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 42888 | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CARRIER/FP-51PMXRACCARP19KEDP3C |  | 51QSXRACCON19KEDN14PC-0558019 | 51PMXRACCAR19KEDB08PC-0070853 |  | Working | Working | Off | 8.1 | 8 |  |  |  | WORKING | Off | Off | DENYO | Working | None | 25 | Working | CF200 | 1631 | None | 354822 | Working | None | 16.5" | 1SMNM697288 | Working | N/A | Working |  |  | Off | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | HARIRS | STRATEX | No | 7177 | 7373 |  | OK | OK | Yes | CAMOTES | LEGACY | ALCATEL | No |  |  |  | OK | OK | Off | SUN TABOGON | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | SUN TABOGON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | FACING AVIAT | 1 | 2G SUN POBLACION | 2 | 2G SMART | 11 | SECOND E1 SUN TABOGON | [6 empty] | ALCATEL | 1 | VACANT | 2 | FIRST E1 2G SUN TABOGON | 4 | SECOND E1 2G SUN TABOGON | [19 empty] | HARRIS | 1 | NMS | 2 | SUN 3G | 3 | 3G | [66 empty] | ELTEK | 54.03 | 1 |  | 4 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 53.6 | 53.6 | 53.6 | 53.6 | Off | [6 empty] | 100 | BTS3900L UPPER | [8 empty] | 63 | DCPDB B | [22 empty] | 16 | RTN950 MAIN |  |  | NOKIA PSSS900 | 54.02 |  |  | 21.6 | 3 | 3 | RITAR | 150 | RITAR | 150 | RITAR | 150 |  |  | Off |  | 51.1 | 50.8 | 50.8 |  | Off | [10 empty] | 32 | ALCATEL |  |  | 16 | RTN950 REDUNDANT |  |  | 80 | BTS3900L LOWER | [39 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 23.2 | 30 | ACU1 | 40 | GSM SUPPLY | 30 | ACU2 | 30 | ELTEK 2 | 20 | LIGHTNING | 30 | ACU 3 | 20 | TOWER LIGHT | 20 | COMBA REPEATER | 70 | ELTEK 1 | 20 | OUTLET | [20 empty] | Done | OK
868 Sunny Hills.pdf | 868 | Sunny Hills | 2017-02-11 | Eric Brian Aligway | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | Ongoing Refarming proj. | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK | Nokia PSSS for replacement | OK |  | N/A |  | OK |  | N/A |  | OK |  | Rectification | Camouflage tower | OK |  | OK |  | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
873 Maribago Checklist.pdf | 873 | Maribago | 2017-02-21 | EDDIE D. CLAVE JR. | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | For re-labelling | Rectification | van leaking for van rehab | OK |  | OK |  | OK |  | N/A | bypass due to high CRC | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | defective genset battery | OK |  | OK |  | Rectification | port hole for sealant | Rectification | unclean surrounding and excess mats on site | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
874 Pajo.pdf | 874 | Pajo | 2017-02-09 | Astrobal A. Trozo | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Off |  | OK |  | OK |  | OK |  | N/A | Bypass due to high CRC | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | Rectification | For fuel line inst | Rectification | Defective ATS | N/A |  | OK |  | OK |  | Rectification |  | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
F13-ALEGRE BEACH RESORT-01252017.pdf | F13 | ALEGRE BEACH | 2017-01-25 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A |  | Brgy Calumboyan, Sogod, Cebu | COMMERCIAL | LOT | PERMANENT | LOT | SST 150FT | Concrete Shelter | 24HRS | CARETAKER | Off |  |  |  | 124.0289 | 10.7887 |  | WORKING | OK | N/A | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | WORKING | OK | Ok | WORKING | OK | OK | Off | LEAKING INSIDE CABIN NEAR RECTIFIER | WACU | Off | Off |  |  |  | DK10PC-0436355 |  |  | Working | Off | Off | [5 empty] | WORKING | Defective | Off | DENYO | Defective | None | 25 | Working | CF100 |  | None | 340361 | Working | None |  |  | Working | N/A | Working |  |  | Off | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | AVIAT | Yes | 7625/8073.845/8133.145 | 7457/7762.45/7821.825 | UNKNOWN/-42.7/-42.9/43.6 | OK | OK | Yes | CATMON | HARRIS | AVIAT | Yes | 7373/8192.445/8251.745 | 7177/7881.125/7940.425 | -0.025626 | OK | OK | Yes | BORBON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | facing catmon | 9 | 2G | [36 empty] | facing catmon | 1 | rack 2 | 2 | rack 5 | 3 | facing borbon p3 | 4 | 3G alegre | [12 empty] | facing borbon | 1 | rack 2 | 2 | rack 5 | 3 | facing catmon p3 | 4 | n/a | [43 empty] | ELTEK 1 | 53.85 | 1 | 7 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53 | 52.9 | 52.7 | 52.6 | OK | 125 | BTS 3900 UPPER | [20 empty] | 40 | PLDT EQUIPMENT |  |  |  |  | 40 | HARRIS DCPDB A | [14 empty] | ELTEK 2 | 53.67 | 0 | 24 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.4 | 53.3 | 53.3 | 53.2 | Off | [18 empty] | 40 | SMART TURBO U2100 DC BREAKER |  |  | 40 | BTS 3900 LOWER | [10 empty] | 20 | HARRIS DCPDB B | [23 empty] | Off | [5 empty] | Off | [44 empty] | 200 | 9 | 30 | ELTEK A2 | 30 | ELTEK A1 | 30 | ELTEK B2 | 50 | ZTE POWER CABINET | 30 | ACU | 50 | N/A | 20 | LIGHTS | 70 | ELTEK B1 | [24 empty] | Done | OK |  |  |  | RECTIFIER | 1 | ZTEZXDU68 /210038495610 | WFM | RECTIFIER | 1 | NOKIA PSSS | WFM | [32 empty] | ELECTROMECHANICAL | CONVENIENCE OUTLET | [5 empty] | ELECTROMECHANICAL | LIGHTS | [5 empty] | ELECTROMECHANICAL | TOWER LIGHTS | [5 empty] | ELECTROMECHANICAL | ATS | 1 | KUTAI | ATS3BC0225 | 220 | 11373 | ELECTROMECHANICAL | EXHAUST FAN | [61 empty] | 2 RECTIFIER FOR ARDA, van leaking for roof repair,no lights inside cabin,outlet not working,new fuel tank delivered,no tower lights,manual genset,defective ats,need additional acu,need replacement rack 30 of aviat due to in-compatible software,DEFECTIVE HARRIS FAN
F46 Pagsabungan PMR.pdf | F46 | Pagsabungan | 2017-01-26 | A. Ambil/G.Vale | OK | VSWR all 1.1. | N/A | NOT APPLICABLE. | OK |  | N/A |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK |  | OK | Done back-up 3G and LTE. | N/A | NOT APPLICABLE. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK |  | N/A | NOT APPLICABLE. | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK | 2 POWERONE RECTIFIER FOR RETIRE. | OK | OK. | N/A | NOT APPLICABLE. | OK |  | Rectification | ATS FOR REPLACEMENT. | OK |  | OK |  | OK |  | Rectification | FOR GRASSCUTTING. | OK |  |  | A |  | Brgy. Pagsabungan, Mandaue City | A | NA | Permanent commercial power. | Last Mile | Guyed Tower 32m | Concrete | 24 hours | via gate/caretaker | Yes | 2018 |  | NA | 10.3584 | 123.9408 | BESIDE the cellsite Brgy. Pagsabungan, Mandaue City | 2, 0 | OK | OK | OK | For CSMP Endo | For grasscutting | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 1, 3 | OK | Ok | none | OK | For Rectification | OK | port hole for sealant | WACU | WACU | Off | CONR19KEDP1C | CONR19KEDP1C |  | 51QSXRACCON19KEDR07PC-0404142 | 51QSXRACCON19KEDh08PC-0404132 |  | Working | Defective | None | 8 | defective/for arda | n/a | Asahi Hitech | Asahi Hitech | 0, 1 | Defective | Defective | Kipor SN: 0717120163 | Defective | None | 60 | None | CF200 | defective | None | VECO 486536 GS | Working | None | 300L | 60 227726 | For CSMP Endo | 0 | Working | ATS FOR REPLACEMENT | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | NONE | NONE | Off | None | BTS3900 | Retrieved | NONE | Off | NONE | Off |  | OK | OK | NONE |  | Off |  |  |  | Off | Off | Off | NONE | NONE |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off | NONE | NONE | [11 empty] | ECI | XDM 100 | No | Trad | Yes | ZTE | ZXMP M721 | No | Trad | Yes | NONE |  | Off | Off | Off | NONE |  |  | NONE |  | NONE | [35 empty] | i3-11 | F46 LTE FD | i3-12 | F46 PABIS | S10-C2 | F46 3G | [35 empty] | 1 | TX FACING CANDUMAN | FOR CHECKING | 2 | RX FACING CANDUMAN | TO FOLLOW | [25 empty] | PowerOne | 54.46 | 0.4 | 29 | 29 | 4 | 3 | Sacred SUN | 180 | Sacred SUN | 180 | Sacred SUN | 180 |  |  | No |  | 53.96 | 53.8 | 53.9 | none | OK | 60 | SPARE | 60 | SPARE | 63 | DCDU1 G1800 | 63 | SPARE | 40 | SPARE | 40 | ZTE REDUNDANT | 16 | XDM100 B | 16 | SPARE | 80 | BTS3900L UPPER | 80 | BTS3900 UPPER | 10 | SPARE | 10 | SPARE | 10 | SPARE | 6 | RRU 850 2 | 6 | RRU 850 1 | 6 | RRU 850 0 | 6 | SPARE | [10 empty] | PowerOne | 54.41 | 0.9 | 31.6 | 31.6 | 3 | 3 | Sacred SUN | 180 | Sacred SUN | 180 | Sacred SUN | 180 |  |  | No |  | 53.8 | 53.5 | 53.7 | none | OK | 60 | SPARE | 60 | SPARE | 60 | L850 | 60 | L850 | 40 | SPARE | 40 | ZTE MAIN | 16 | SPARE | 16 | XDM 100 A | 16 | SPARE | 10 | SPARE | 10 | SPARE | 10 | SPARE | 10 | SPARE | 6 | SPARE | 80 | BTS3900L LOWER | 80 | BTS3900 LOWER | 6 | SPARE | [10 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | POWERONE A | 70 | POWERONE B | 50 | SPARE | 50 | SPARE | 40 | SPARE | 40 | SPARE | 40 | ACU1 | 40 | ACU2 | 30 | PERIMETER LIGHT | 30 | TOWER LIGHT | 20 | OUTLET | 20 | LIGHTS | [16 empty] | Done | OK |  | P.Quijano | 42761 | ACU | 1 | Condura SN: 51QSXRACCON19KEDh08PC-0404132 | WFM | [36 empty] | Support | ATS | 1 | KUTAI | ATS3BC0225 | 225 A | 10337 | Support | Genset | 1 | Kipor | KDE60SS3 | 60 | 717120163
F55-Nivel Hills-03032017.pdf | F55 | Nivel Hills | 2017-03-03 | Lemuel B. Balbuena and Alan Mark B. Rodrigo | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK | Guy Pole | OK |  | OK |  | OK |  |  | B | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
F58 Pitos1.pdf | F58 | Pit-os | 2017-01-28 | Eric Brian Aligway | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | Facing 820 Talamban RAC1 -42.1 RAC2 -47.2 | OK | Def. NPC card | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | Huawei CEN | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK | Eltek rectifier need additional 2 Banks, SacredSub 180ah | N/A | Need TVSS | OK |  | OK |  | OK |  | OK |  | Rectification | Def. 1 exhaust fan | Rectification | Toilet for repair | OK |  |  | B |  | Brgy. Pit-os, Cebu City |  |  | SST 3 legged |  | 50m | Concrete Cabin | 24/7 |  | No |  | Joel Atamosa |  | 123.9205 | 10.399 | Brgy. Pit-os, Cebu City |  | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | Off | OK | Expired | OK | Busted 1 fluorescent light buld | OK | Ok | No Emergency light | OK | OK | OK |  | WACU | WACU | Off | CQXRT195BA | WCONX019ED1 |  | 48410411 | 51QSXRACCON19KEDF15PC-0370763 |  | Working | Working | Off | [5 empty] | Wo | Defective | Working | Powercity | Working | None | 45 | Working | CF200 | 6695 | None | 450453 GS6 | Working | None | 12" |  | Working | NONE | Working | Genset need fuel, fuel sock 12" old stocks | Huawei | Retrieved | H | Retrieved |  | Retrieved |  | Retrieved |  | Off | Boser 2U | 6 | Retrieved | None |  | Retrieved |  | Retrieved |  | Off |  | OK | OK | Aviat |  | Yes | 12933 | 13199 | 0.89407 | OK | OK | Yes | 820 Talamban |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | Bro(DAC GE) |  |  | 3 | LTE(DAC GE) | [25 empty] | 6 | TX umts(Huawei CEN)U850,U2100,U900 | 7 | TX GSM(Huawei CEN) 900B | [37 empty] | Eltek | 54.14 | 5A |  | 77A | 4 | 2 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No | 2 | 54.1V | 54.1V |  |  | Off | 100 | DCDU 12B-A1 | 100 | DCDU 12B/L1800/L700 |  |  | 100 | BTS 3900 LOWER | 63 | huawei dcdu LTE TDD | [16 empty] | 40 | Huawei CEN B |  |  | 20 | Harris B | [6 empty] | 63 | RRU2 | 63 | RRU1 | 63 | RR0 | PowerOne | 54.2V | 2.8A | 36.1A | 39.3A | 2 | 6 | [8 empty] | No | 6 | 54.2V | 54.2V | 54.2V | 54.2V | OK | [6 empty] | 63 | Huawei 3G/LTE |  |  | 40 | Bro ABB | [6 empty] | 10 | Harris A | [16 empty] | 80 | BTS 3900 UPPER | [21 empty] | Off | [5 empty] | Off | [44 empty] | 125 |  | 150 | Eltek1 | 150 | Eltek2 | 70 | Spare |  | Vacant | 40 | ACU2 | 40 | ACU1 | 30 | Spare | 70 | PowerOne | 20 | Spare |  | Vacant | 20 | Lights | 20 | C.O | [16 empty] | Done | OK | PowerOne Need addtional RM |  | 2017-01-28 | Huawei BTS3900 | 1 |  | FO | ACU 2hp | 1 | 140788 | WFM | Nokia PSSS | 1 |  | WFM | Kutai ATS | 1 |  | WFM | Huawei BTS 3012 | 1 |  | Build | [20 empty] | MWR-HARRIS | NPC | 1 | Aviat |  |  |  | Civil | Fuel line | [5 empty] | Cable Ladder
F59 Bacayan1.pdf | F59 | Bacayan | 2017-01-31 | Eric Brian Aligway | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | Eltek1 control module def. | OK |  | N/A |  | OK |  | Rectification | Def. ATS | OK |  | OK |  | Rectification |  | OK |  | OK |  | Percival Quijano | B | 2017-01-31 | Brgy. Bacayan, Cebu City |  |  | Commercial Power |  | 140ft. | Collapsible Van | 24/7 |  | Yes |  | Gabby Lesson |  | 123.9143 | 10.3834 | Brgy. Bacayan, Cebu City | Perimeter light grounded for rewiring | OK | OK | OK | For CSMP Endo | Access to main gate due ongoing land development | Defective | OK | Off | OK | OK | OK | OK | OK | OK | OK | Busted fluorescent buld | OK | Ok | No emergency light | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019KED |  | 51QSXRACCON19KEDF15PC-0756732 | 51QSXRACCON19KEDF15PC-0370747 |  | Working | Working | Off | [5 empty] | Working | Defective | Defective | Powercity | Defective | None | 45 | Working | CF100 | 66.5 | None |  | Working | None | 400li. |  | Working | NONE | Working |  | Huawei | Retrieved |  | Off | Huawei | Retrieved | Huawei | Retrieved |  | Off |  | 6 | Retrieved | None | Huawei | Retrieved |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 15 | WIMAX(MCSM) | 16 | 2G PBis(MCSM) | [68 empty] | Eltek | 53.8 | 1Amp. |  | 46Amp. | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 54 | 53.4 | 53.7 | 53.9 | OK | 100 | DCDU 12B | [6 empty] | 63 | DCDU | [8 empty] | 40 | XDM100 A | 40 | ZTE FS Main | [21 empty] | FMS TB Lock | Eltek | 54.3 |  |  |  | 4 | 4 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | SacredSun | 180 | No |  | 54.3 | 54.4 | 54.2 | 54.1 | OK | 100 | Wimax |  |  |  |  | 100 | BTS3900 Upper | [10 empty] | 40 | XDM100 B | 40 | ZTE FS Redundant | [6 empty] | 40 | CMM | [6 empty] | 16 | FMS Batt meter | 16 | RRU0 | 16 | RRU1 | 16 | RR2 | [15 empty] | Off | [5 empty] | Off | [44 empty] | 100 |  | 70 | Eltek1 1-1 | 70 | Spare | 50 | Elek1 1-2 | 50 | Eltek2 2-2 | 40 | Spare | 40 | Spare | 40 | Spare | 40 | Spare | 30 | ACU2 | 30 | ACU1 | 30 | Spare | 30 | Perimeter lights | 20 | lights | 20 | CO | 70 | Eltek2 2-1 | 70 | Exhaust Fan | [8 empty] | Done | OK |  |  |  | PowerOne Rec | 1 |  | WFM | Nokia PSSS | 1 |  | WFM | [32 empty] | EXHAUST FAN |  | 2 |  |  |  |  | PERIMETER LIGHTING | [6 empty] | ATS | [6 empty] | Rectifier | Control module | 1 |  |  |  |  | RIGHT OF WAY
F60 Lamac.pdf | F60 | Lamac | 2017-02-20 | A. AMBIL | OK | ALL ARE 1.1 TO 1.4. | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK | DONE FOR 3G AND FD LTE | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification |  | OK |  | OK |  | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 42786 | BRGY. LAMAC, CONSOLACION | RESIDENTIAL | LOT | PERMANENT | LOT | GUYED 32M | VAN | 24H | CARETAKER | Yes |  | RENIE ALIVIO | 9282590857 | 123.9648 | 10.3877 | BRGY LAMAC, CONSOLACION | 2, 0 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 1, 1 | OK | Ok | 0, 1 | OK | OK | Off |  | WACU | WACU | Off | WCONH019ED | WCONX019ED1 | NONE | 51QSXRACCON19KED J16PC-0974997 | 51QSXRACCON19KED K15PC-0540073 | NONE | Working | Working | None | 7.8 | 7.9 | NONE | ASAHI | ASAHI | 0, 1 | Defective | Defective | DENYO | Working | Working | 25 | Working | CF200 | 9710 | Working | VECO 472412 GS6 | Working | None | 500 | 72139527 | For CSMP Endo | 0 | Working | DENYO GENSET SN: 5445668, KUTAI SN: 8339 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | NONE | Off | BOSER | 6 | Retrieved | Off | BTS3900 | Retrieved | NONE | Off | NONE | Off |  | OK | OK | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | XDM-100 | Yes | Trad | Yes | ZTE | ZXMP M721 | Yes | Trad | Yes |  |  | Off | Off | Off |  |  |  | NONE | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | ECI XDM-100 | i5-9 | bro router | i5-11 | F60 LTE FD | i5-16 | F60 2G PABIS | [14 empty] | ZTE FS | s10-c1 opt | F60 Lamac 3G | [18 empty] | CORE 5/6 | FACING TABOK | UNKNOWN | CORE 1/2 | FACING PMANDAUE | UNKNOWN | [25 empty] | POWERONE | 54.3 | 0 | 49 | 49 | 3 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.9 | 53.9 | 53.9 | 53.9 | OK | 50 | HDX FEED A | 50 | SPARE |  | VACANT | 80 | HUAWEI BTS UPPER | 40 | SPARE | 40 | SPARE | 16 | SPARE | 16 | XDM100 POWER B | 16 | ZTE FS | 80 | REFARMING U2100/G1800 |  | VACANT | 80 | REFARMING L850 |  | VACANT | 6 | SPARE | 6 | RRU0 | 6 | RRU1 | 6 | RRU2 |  | VACANT |  | VACANT | [6 empty] | POWERONE | 54.4 | 0 | 33 | 33 | 3 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | No |  | 53.8 | 53.8 | 53.8 | NONE | Off | 50 | FAILSAFE ULTRACAB | 50 | SPARE | 63 | LTE FDD | 63 | SPARE | 40 | SPARE | 40 | SPARE | 16 | SPARE | 16 | XDM100 POWER A | 16 | ZTE FS REDUNDANT | 10 | SPARE | 10 | SPARE | 10 | FMS | 10 | SPARE | 10 | SPARE | 80 | HUAWEI BTS3900 LOWER | 10 | SPARE | 10 | SPARE | [25 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 70 | POWERONE | 70 | POWERONE | 50 | SPARE | 50 | SPARE | 40 | SPARE | 40 | ACU1 | 40 | SPARE | 40 | ACU2 | 30 | SPARE | 30 | SPARE | 20 | SMART BRO BBU | 20 | SPARE | [16 empty] | Done | OK | POWERONE1 SN:7N074447690 POWERONE2 SN:7N073814240 | PERCIVAL QUIJANO | 42786 | [40 empty] | SUPPORT | GENSET | 1 | DENYO |  | 25 | PLS SEE ABOVE | [84 empty] | Defective genset.
F62 San Antonio.pdf | F62 | San Antonio | 2017-03-24 | Eric Brian Aligway | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Off |  | OK |  | Rectification | Def. ATS | OK |  | OK |  | Rectification | Cabin flooring for repair | OK |  | OK |  |  | B | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 3G (allied SW) | 2 | 2G (allied SW) | 3 | LTE (allied SW) | [81 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
F63-BEverly Hills-02072017.pdf | F63 | BEVERLY HILLS | 2017-02-07 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | NOT BOLTED PROPERLY | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | PRIME SITE | N/A | PRIME SITE | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PRIME GENSET | LOT | MONOPOLE 80FT | CONCRETE ROOM | 24HRS | CARETAKER | Yes | [6 empty] | WORKING | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-03-04 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA | CONDURA |  | DN10PC-0470090 | T15PC-0741941 |  | Working | Working | Off | 8 |  |  |  |  | WORKING | Defective | Off | KIPOR | Working | None | 45 | Working | CF100 |  | None |  | Working | None |  |  | Working | N/A | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI/U2100/900 | Retrieved |  | Off |  | Off | BOSER | 6 | Off | Off | HUAWEI/850/2100 | Retrieved | HUAWEI/3500 | Retrieved |  | Off |  | OK | OK | HARRIS | STRATEX | Yes |  |  |  | OK | OK | No | NIVEL HILLS | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | No | NIVEL HILLS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | APPOLLO | Yes | Trad | Yes | ECI | XDM100 | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK | 54 | 3 | 75 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 51.2 | 51.1 | 50.9 |  | OK | 100 | DCDU 1 | 100 | BTS 3900 Lower | 100 | dcdu 2 | 100 | DCDU 3 | [10 empty] | 40 | LTE-TDD DCDU | 40 | HARRIS B | 40 | XDM100B | 40 | BRO ABB | [10 empty] | 16 | FMS | 16 | RTN950 Main | 16 | CP10 | 16 | ECI APOLLO SOURCE B | ELTEK OLD | 54.1 | 1.9 | 19.8 |  | 5 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | No |  | 53.4 | 53.3 | 53.2 |  | Off | [10 empty] | 50 | Harris A | 50 | 3G/LTE PWR DCDU | [8 empty] | 16 | XDM 100A | 16 | ECI APOLLO OPT9603 SOURCE A | 16 | ALLIED SWITCH | 16 | RTN950 REDUNDANT | [12 empty] | 6 | FMS | [15 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 32.9 | 70 | ELTEK 1 | 70 | ELTEK 2 | 40 | ACU 2 | 40 | ACU 1 | 20 | C.O | 20 | TOWER LIGHT | 20 | RADIO ROOM | 70 | ELTEK OLD | [24 empty] | Off | Off |  |  |  | ATS | 1 | KUTAI/8695 |  | CABINET | 1 | BTS3900 |  | AIRCON | 1 | CARRIER/48410595 |  | RECTIFIER | 1 | NOKIA/7P034755434 |  | BATTERY | 3 BANKS | LYNX
F68 Pajak.pdf | F68 | Pajak | 2017-02-06 | Eddie D. Clave Jr. | OK |  | OK |  | Off |  | N/A |  | OK | Surge supressor bypass due to high crc errors | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | for re-labeling | OK |  | OK |  | OK |  | OK |  | N/A | bypass due to high crc | OK |  | OK |  | Rectification | no frequency indicated on the label | Rectification | no ne label for eci xdm100 | Rectification | for regrooming by PLDT | N/A |  | N/A |  | N/A |  | Rectification | 1 eltek rectifier with defective slots; only 3 RM can be accomodated | OK |  | N/A |  | OK |  | Rectification | no ats; powercity genset noisy | N/A |  | OK |  | Rectification | for port hole sealant | Rectification | garbage for pull-out by CSMP; excess mats for ARDA | OK |  |  | B | 2017-02-06 | Brgy. Pajak, Lapu-Lapu city | Residential | Lot | Prime Genset | Lot | Guyed; 110ft | Van | 24hrs | Caretaker | No | [6 empty] | 0/4 | Off | OK | Off | For CSMP Endo |  | Off | OK | OK | Off | OK | OK | Off | OK | OK | OK | 2017-01-04 | OK | Ok | 0/1 | For Tagging | For Rectification | For CSMP Endo |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | Eltek | 54.06 | 6 | 13 | 13 | 3 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No | [5 empty] | OK | [8 empty] | 63 | Vapel A |  |  |  |  | 63 | Smart Bro B | [6 empty] | 40 | ECI Apollo B | [12 empty] | 16 | XDM100 B |  |  |  |  | 16 | RTN950 Main facing Sun Pajac | Eltek | 53.73 | 6 | 78 | 78 | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No | [5 empty] | OK | 100 | 2g Lower | 100 | Refarm 2100 & u900 | 100 | Refarm L850 & G1800 | 100 | Refarm G1800 | 63 | LTE-FDD |  |  |  |  | 63 | 2g Upper |  |  | 40 | LTE TDD DCDU | [6 empty] | 40 | Allied SW | 40 | XDM100 A | 20 | ECI Apollo A | 20 | Bro A | 20 | RTN950 Redundant | 16 | FMS | 16 | RRU 0 | 16 | RRU 1 | 16 | RRU 2 | [15 empty] | Off | [5 empty] | OK | [86 empty] | Off | Off
F70 LiloanTP.pdf | F70 | LiloanTP | 2017-02-07 | G.Vale/A. Ambil | OK | All VSWR are 1.1 and 1.2. | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK | No MW, MW recovered during PMR. | N/A | NOT APPLICABLE. | OK |  | OK |  | OK | Done for 3G/TD/FD. | N/A | NOT APPLICABLE. | OK |  | OK | OK. | OK |  | OK |  | OK |  | N/A | NONE. | OK |  | OK |  | N/A | NOT APPLICABLE. | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK |  | OK |  | Rectification | 1 HOUR BATTERY BACK-UP SINCE PRIME SITE. LOADED SITE. | N/A | NOT APPLICABLE. | OK | 2 PERKINS GENSET WORKING. | OK | GENSETS ARE OK. NO ATS SINCE PRIME SITE. | N/A | NOT APPLICABLE. | OK | tower light defective | OK |  | OK |  | OK |  | Percival Quijano | B | 42773 | Aranas Riverside Project, Landing, Catarman, Liloan, Cebu | Residential | Lot | Prime Genset | Lot | GUYED 32metersLot | Van | 24 hours | CARETAKER | Yes | 2017 | Benjie Aranas | NOT AVAILABLE | 10.3945 | 123.9993 | Catarman, Liloan Cebu | 1, 1 | OK | for CSMP Endo | OK | For CSMP Endo | need quotation for repair of fence | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4, 0 | OK | Ok | 1, 0 | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 | NONE | 51QSXRACCON19KED F12PC-0261755 | 51QSXRACCON19KED C12PC-0174100 |  | Defective | Working | Off | 2 | 7.5 | N/A | ASAHI | ASAHI | 2, 1 | Defective | Defective | PERKINS/PERKINS/POWERCITY | None | Working | 25/25/25 | None | Off | G1-32H, G2-4680H G3-4026H | None | N/A | Working | None | 1800L | N/A | Working | 0 | Working | PERKINS1 SN: 201605904080, PERKINS2 SN:20151290235 , POWERCITY SN: G14070694 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | BOSER | 6 | Retrieved | None | BTS3900 | Retrieved | BTS3900 | Retrieved | N/A | Off |  | Off | Off | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE | [7 empty] | ECI | XDM-100 | Yes | Trad | Yes | ECI | APOLLO | Yes | Trad | Yes | N/A |  | Off | Off | Off |  |  |  | NONE | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | ECI XDM-100 AND ECI APOLLO FS | i5-12 | F70 LILOANTP 2G (TO GTMU) | i5-13 | F70 LILOANTP BRO (TO BOSER PORT1) | u0/0 | F70LILOANTP LTE TDD (TO UMPTb2) | u0/1 | TRUNK TO PMANDAUE (TO Allied P21) | [12 empty] | ALLIED SWITCH | 3 | F70 LILOANTP LTE FDD (TO UMPTa2) | 4 | F70 LILOANTP LTE 3G (TO UMPTB1) | 21 | TRUNK TO PMANDAUE (TO u0/1) | [14 empty] | 42737 | acing PLDT Mandaue | unknown | 42861 | facing 804 Liloan Calero | unknown |  |  |  | 42737 | ECI FS facing 802 Compostela | unknown | 42798 | ECI FS facing V3530 Danao Suba | unkwon | [16 empty] | ELTEK | 53.63V | 0 | 16 A | 16 A | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE |  | No |  | 53.6 | 53.5 | 53.4 | NONE | OK | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | ECI XDM100 SOURCE B | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | 3G 850 | 40 | LTE TDD | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SPARE | 16 | SPARE | 16 | ECI FS SOURCE B | 16 | ABB | 16 | FMS | ELTEK | 54.6 | 1A | 65 | 65 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.9 | 53.7 | 53.5 | 53.4 | OK | 100 | SPARE | 100 | SPARE | 100 | DCDU L850/U2100 | 100 | 2G LOWER | 63 | ECI XDM100 A | 63 | SPARE | 63 | SPARE | 63 | 2G UPPER | 63 | LTE FDD | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | ECI APOLLO FS B | 40 | SPARE | 40 | BRO ROUTER | 20 | FMS | 20 | SPARE | 20 | SPARE | 16 | ALLIED TURBO SW | 16 | SPARE | 16 | SPARE | 16 | SPARE | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK NEW 1 | 70 | ELTEK 1 | 50 | ELTEK NEW 2 | 50 | ELTEK 2 | 40 | SPARE | 40 | SPARE | 40 | PERIMTER LIGHT | 40 | TOWERLIGHT | 30 | CABIN LIGHT | 30 | CO | 30 | ACU2 | 30 | ACU1 | 20 | SPARE | 20 | SPARE | [12 empty] | Done | OK |  | PERCIVAL QUIJANO | 42773 | SUPPORT | 12 PCS | SACRED SUN 180AH BATTERY | WFM
F89-TUBURANTP-03302017.pdf | F89 | TUBURAN | 2017-03-30 | JEROME BUTONG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT |  | LOT | 3-SST 150FT |  | 24HRS | CARETAKER | Off | [6 empty] | WORKING | OK | OK | OK | OK |  | Defective | OK | Off | OK | OK | Off | OK | OK | OK | OK | 42888 | OK | Ok | DEFECTIVE | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CONDURA/WCONX019ED1 |  | 51QSXRACCON19KEDB15PC-0154242 | 51QSXRACCON19KEDT15PC-0756882 |  | Working | Working | Off | 7.8 | 8 |  | ASAKI |  | WORKING | Defective | Off | POWERCITY | Working | Working | 25 | Working | Off | 156.7 | None |  | Working | Off |  |  | Working | 2 | Working | GENSET FOR TRANSFER TO GENSET PAD | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes | 12905 | 13173 | 0.84444 | OK | OK | Yes | FACING PLDT TUBURAN |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | FACING TUBURAN | 1 | 1ST E1 2G | 7 | 2ND E1 2G | 8 | 3RD E1 2G | [33 empty] | S3 P2 | 3G | [70 empty] | ELTEK | 53.95 |  |  | 22 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 50.6 | 50.5 | 50.4 | 50.4 | Off | [6 empty] | 100 | BTS3900L UPPER | [28 empty] | 16 | HARRIS A | [6 empty] | NOKIA | 53.7 |  | 25.6 |  | 4 | 2 | SACREDSUN | 300 | SACREDSUN | 300 |  |  |  |  | Off |  | 51.5 | 51.5 |  |  | Off | [6 empty] | 50 | 3G |  |  | 16 | HARRIS B |  |  |  |  | 100 | BTS3900L LOWER | [41 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 20.63 | 70 | EMPOWER | 70 | ELTEK 1 | 50 | ELTEK 2 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | FAN | 30 | ACU 2 | 20 |  | 30 | ACU 1 | 20 | LIGHTINGS | 20 | C.O | [12 empty] | Done | OK | 2 NEW ACU FOR INSTALLATION OR TRANSFER, GENSET FOR TRANSFER TO BASEMENT PAD, 1 GENSET FOR ARDA, 2 ACU FOR ARDA, MICROWAVE RADIO FOR ARDA, FOR GRASSCUTTING, EXCESS MATERIALS.17Q1-1948.
F90-TABUELAN-03292017.pdf | F90 | TABUELAN | 2017-03-29 | JEROME BUTONG | Rectification | with vswr alarm mrfu 900b sec2 | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | genset wont start w/ ecall | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | 3-SST 150FT | CONCRETE ROOM | 24HRS | CARETAKER | Yes | [6 empty] | WORKING | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36678 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CONDURA/FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDT15PC-0755064 | 51QSXRACCON19KEDR10PC-0505774 |  | Working | Working | Off | 7.8 | 8 |  |  |  | defective | None | Off | DENYO | Defective | None | 25 | Working | CF200 | 4453 | Defective |  | Working | None |  |  | For CSMP Endo | n/a | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | ANAPOG | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | PLDT TUBURAN | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | ANAPOG EXPANSION |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | ELTEK | 53.61 |  |  | 38 |  |  | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 53 | 53 | 52.9 | 52.9 | For Rectification | [20 empty] | 40 | DCPDB B | [22 empty] | ELTEK | 53.39 |  |  | 8 |  |  | SACREDSUN | 180 | SACREDSUN | 180 |  |  |  |  | Off |  | 50.7 | 50.5 |  |  | For Rectification | 100 | BTS3900 UPPER | 100 | BTS3900 LOWER |  |  |  |  | 63 | DCDU 3G | [8 empty] | 40 | DCPDB A | [22 empty] | 16 | FMS | [15 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 20.18 | 100 | ELTEK 1 | 100 | ELTEK 2 | 50 | GSM900 NOT USED | 60 | SPARE | 30 | ACU 2 | 30 | ACU 1 | 30 | SPARE | 30 | SPARE | 30 | SPARE | 30 | SPARE | 20 | OUTLET | 20 | LIGHTING | [16 empty] | Done | OK | 2 BANKS LYNX FOR ARDA, 2 NCC FACING ANAPOG AND PLDT TUBURAN WITH POWER CONCERN ISSUES, NO TOWER LIGHT, NO PERIMETER,DEFECTIVE GENSET WITH ECALL, 2 ELTEK WITH RM ISSUES.17Q1-1908
F92 Labogon.pdf | F92 | Mandaue Labogon | 2017-02-15 | A. Ambil | OK | All are ok 1.1 to 1.2. | OK |  | OK |  | N/A | NOT APPLICABLE | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | done for 3G/LTE FD. | OK | All -36dBb. | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | PowerOne cntroller defective/for replacement. | OK |  | OK |  | OK |  | Rectification | ATS defective | OK |  | OK |  | OK |  | Rectification | Needs grasscutting | OK |  | Percival Quijano | B | 42781 | Brgy Labogn, Mandaue city | Commercial | Lot | Permanent | Lot | Guyed 32m | Van | 24H | Caretaker | Yes |  | unknown | unknown | 123.9573 | 10.3514 | unknown | 3, 0 | OK | OK | OK | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | Off | OK | OK | 1, 7 | OK | Ok | none | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 | NONE | 51QSXRACCON19KED B15PC-0167129 | 51QSXRACCON19KED T15PC-0755059 |  | Working | Working | Off | 7.9 | 7.9 | N/A | ASAHI | ASAHI | 1, 0 | Defective | Defective | DENYO | Defective | None | 45 | Working | CF100 | 4421 | None | TAP TO NEIGHBOR | Working | None | 100L | TAP TO NEIGHBOR | Working | NONE | Working | DENYO SN: 3717701, ATS: Kutai SN: 8708 (defective) | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | NONE | Off | BOSER | 6 | Retrieved | None | BTS3900 | Retrieved | NONE | Off | NONE | Off |  | OK | Off | HUAWEI | RTN950 | Yes |  |  | -36dBm | OK | OK | Yes |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off |  | Off |  | none |  |  |  | none |  |  |  | none |  |  |  | ZTE |  | Yes | Trad | Yes | ECI | XDM-100 | Yes | Trad | Yes | NONE |  | Off | Off | Off |  | NONE |  | NONE | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | ECI XDM-100 | i5-10 | SMARTBRO | i5-11 | F92 LABOGON LTE FD | i5-12 | f92 Labogon 2g pabis | i5-13 | V3447 PABIS (to RTN950 EG4 slot6-P4) | i5-14 | f92 wimax | i5-16 | rtn950 nms | [8 empty] | RTN950 FACING V3447 | S6-P2 optical | 3G Aggregate (to ZTE S10-C1) | S6-P3 | F92 LABOGON 3G TO UMPTb2 | S6-P4 | V3447 2G PABIS FROM i5-13 | S1-P1 optical | LTE FD Aggregate (to ZTE S9-C1) | [12 empty] | core 9/10 | facing Tabok | unknown | core 2/4 | facing Basak | unknown | [25 empty] | POWERONE | 53.3 | 0 | 25 | 25 | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 | NONE |  | NONE |  | No |  | 53.5 | 51 | NONE | NONE | OK | 100 |  | 100 |  | 63 | ZTE PDU MAIN | 63 | PLDT AG B | 40 | ECI XDM100 SOURCE B | 40 | SPARE | 16 | FOR VERIFICATION | 16 | RTN950 FACING BASAK MAIN | 16 | ZTE FS MAIN | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | [14 empty] | AT RECTIFIER 3 | [14 empty] | Off | [5 empty] | Off | [44 empty] | ELTEK | 54.04 | 0 | 94 | 94 | 3 | 2 | SACRED SUN | 180 | SACRED SUN | 180 | N/A |  | N/A |  | No |  | 52.9 | 51.9 | NA | NA | Off | 100 | ZTE WIMAX B | 100 | DCDU1 | 100 | DCDU2 | 100 | 2G LOWER | 63 | PLDT AG A / BRO ABB | 63 | ECI B | 63 | HUAWEI LTE U2100 | 40 | VACANT | 40 | ZTE FS MAIN | 40 | SPARE | 40 | SPARE |  |  | 80 | FOR VERIFICATION | 20 |  | 20 |  | 20 |  | 16 | RTN950 REDUNDANT FACING BASAK | 16 |  | 16 |  | 16 | [5 empty] | 100 | 100 | 70 | SPARE | 70 | POWERONE | 50 | SPARE | 50 | ELTEK2 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 30 | SPARE | 30 | ACU1 | 30 | LIGHT | 30 | ACU2 | 70 | ELTEK1 | 20 | CO | [12 empty] | Done | OK | ELTEK SN: 120124101210 POWERONE SN: 7N060260750 | PERCIVAL QUIJANO | 42781 | [40 empty] | SUPPORT | ATS |  | KUTAI |  |  | 8708
F94 Babag.pdf | F94 | Babag | 2017-01-10 | Astrobal Trozo | OK |  | OK |  | OK |  | N/A |  | Rectification | Surge supressor bypass due to high CRC | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | Rectification | for label replacement | OK |  | OK |  | OK |  | OK |  | N/A | Surge supressor bypass due to high CRC | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | for load transfer of L700 to another Eltek; For decommission of Powerone | Off |  | N/A |  | OK |  | Rectification | Defective ATS. Prime site. | N/A |  | OK |  | Rectification | port hole for sealant; defective exhaust fan; excess materials for pull-out/ARDA | OK |  | OK |  |  | Off
J53-LUYANG TABUELAN-03292017.pdf | J53 | LUYANG TABUELAN | 2017-03-29 | JEROME BUTONG | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | BUILDING | 3-SST 150FT | CONCRETE ROOM | 24HRS | CARETAKER | Yes | [6 empty] | WORKING | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36678 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CONDURA/FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDT15PC-0756709 | 51QSXRACCON19KEDA10PC-0003032 |  | Working | Off | Off | 8.6 | 8.1 |  |  |  |  | None | Off |  | None | None |  | None | CF200 |  | None |  | Off | None |  |  | Off |  | Off |  |  | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | HARRIS | STRATEX | Yes | 7373 | 7177 | 0.93023 | OK | OK | Yes | FACING ANAPOG |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | S7 P2 | LUYANG 2G 1ST E1 | [109 empty] | ELTEK | 53.92 | 0 |  | 1 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 53.6 | 53.6 | 53.5 | 53.5 | OK | 100 | BTS3900L LOWER | [6 empty] | 63 | HARRIS B | [34 empty] | ZTE | 54.5 |  |  |  | 13.3 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | Off | [5 empty] | OK | [16 empty] | 50 | HARRIS A | [8 empty] | 80 | HUAWEI BTS3900L LOWER | [31 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 14.28 | 70 | ZTE RECTIFIER | 40 | SPARE | 70 | ELTEK 1 | 40 | ELTEK 2 | 50 | SPARE | 32 | PERIMETER LIGHTS | 50 | SPARE | 32 | TLO | 40 | ACU 1 | 20 | L.O | 40 | ACU 2 | 20 | C.O | [16 empty] | Done | OK | FOR GRASSCUTTING/1 NEW ACU FOR INSTALLATION OR DIVERSION/1 ACU FOR ARDA/1 PORTABLE GENSET ONSITE NOT WORKING FOR ARDA/3 BANKS POWERSAFE FOR ARDA 17Q1-1889
J71 Gunob Checklist.pdf | J71 | Gun-ob | 2017-02-15 | Astrobal Trozo | OK |  | OK |  | Rectification | stolen outdoor grounding busbar | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK | Facing SM Aguaverder ISV3-3=-30.9dBm(TX:14543 RX: 14963); Facing V3445 ISV3-3=-31.9dBm(TX:14529 RX:14949) ISV3-4=-32dBm(TX:14645 RX:15065) ISV3-5=-30.6dBm(TX:14627 RX:15047) | OK |  | Rectification | excess materials for pull-out; defective van, perimeter & tower lights | Rectification | stolen outdoor grounding busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Rectification | missing power cable for powerone battery bank | OK |  | Rectification | defective TVSS(JSP) | OK |  | Rectification | defective ATS and genset(stolen parts) | OK |  | OK |  | Off | port hole for sealant; defective van door | Rectification | unclean surrounding | OK |  |  | B | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
K89-PORT AREA-01122017.pdf | K89 | Port Area | 2017-01-12 | Lemuel Balbuena | OK |  | N/A |  | OK |  | Off |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | A | 2017-01-12 |  | COMMERCIAL | ROOFTOP | SUBMETER | Inhouse A1 | SST 50FT | ROOM | 8:00 AM-5:00 PM | ADMIN BLDG SECURITY/ROVING GUARD | Yes | [6 empty] | n/a | N/A | N/A | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | All Working | OK | Ok | Not Working | OK | OK | Off |  | WACU | WACU | Off | Condura/WCONX019ED1 | Condura/WCONX019ED1 |  | 51QSXRACCONN19KEDT15PC-0715640 | 51QSXRACCONN19KEDN14PC-0568056 |  | Working | Working | None | 8:00 | 7.5 A |  | Asahi/EM-123 | Asahi/EM-123 | NONE | Defective | Defective | NONE | None | None | NONE | None | Off | NONE | None |  | None | None | NONE |  | Off | NONE | None |  | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | HUAWEI BTS3900L | Retrieved | NONE | Off | NONE |  | Off | Off | HUAWEI BTS3900 | Retrieved | NONE | Off | NONE | Off |  | OK | OK | HUAWEI | RTN950 | Yes | 14711/14641/14585 |  | 32.4/30.6/34.4 | OK | OK | Yes | SAN ROQUE 2 | HUAWEI | RTN950 | Yes | 7777.35/7836.65/7807 | 8088.67/8147.97/8118.32 | 32.5/32.9/32.6 | OK | OK | Yes | SAN ROQUE 4 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ZTE FS | ZXMP M721 | Yes | Trad | Yes | ECIX | XDM100 | Yes | Trad | Yes | NONE |  | Off | Off | Off |  |  |  | N/A | [12 empty] | N/A | [12 empty] | N/A | [10 empty] | ECI XDM100 MCSM i3 | 9 | K89 LTE | 11 | K89 2G | 12 | trunk v3470 san roque2 | p14 | NMS rtn950 | [12 empty] | RTN 950facing v3470 san roque2 EG4 | P1 | VACANT | P2 | trunk eci p12 | P3 | 3G k89 | P4 | trunk v3701 | [12 empty] | 1 | FACING PILTEL MABOLO |  | 2 | FACING PILTEL MABOLO |  | 7 | FACING T.PADILLA |  | 8 | FACING T.PADILLA | [20 empty] | ELTEK | 54.14 | 0 | 8 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No | NONE | 53.9 | 53.9 | 53.9 | 53.9 | OK | [18 empty] | 40 | ZTE FS REDUNDANT | [10 empty] | 20 | ECI B |  |  |  |  | 16 | RTN 950 FACING SAN ROQUE 2 MAIN |  |  |  |  | 16 | RTN 950 FACING SAN ROQUE 4 REDUNDANT | ELTEK | 54.06 | 1 | 77 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.9 | 53.9 | 53.9 | 53.9 | Off | 100 | 2G UPPER | 100 | 2G LOWER | 100 | U2100/G1800 | 100 | L850 | [10 empty] | 40 | BTS3900 | 40 | ZTE FS MAIN | [14 empty] | 16 | ECI A | 16 | RTN 950 FACING SAN ROQUE 2 REDUNDANT |  |  | 16 | RTN 950 FACING SAN ROQUE 4 MAIN | [15 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 17.3 | 70 | ELTEK 2A | 70 | ELTEK 1A | 50 | ACU2 | 50 | ACU1 | 40 | ELTEK 1B | 40 | DC FAN | 40 | C.O | 40 | LIGHTS | 32 | ELTEK 2B | 32 | TOWER | 20 | SPARE | 20 | SPARE | [16 empty] | Done | OK |  |  | 2017-01-12 | RECTIFIER | 1 | POWERONE/7N080567918 | WFM | [36 empty] | ANTENNA SYSTEM | ANTENNA GROUNDING | [5 empty] | ELECTROMECHANICAL | EXHAUST FAN | 2 | ASAHI | EM-12S | 230V-60HZ | 4806514762313 | [77 empty] | FOR ARDA
K92-CASALS-02222017.pdf | K92 | CASALS | 2017-02-22 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A | POLE | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | ROOFTOP | SUBMETER | BUILDING | POLE | ROOM | 8AM-5PM | ADMIN/BLDG SECURITY | Yes | [6 empty] | N/A | Off | Off | Off | Off | BUILDING SITE | Off | Off | Off | Off | Off | Off | Off | OK | OK | OK | 2000-04-01 | OK | Ok | 2000-01-01 | OK | OK | For CSMP Endo |  | WACU | WACU | Off | CONDURA | CONDURA |  | 51QSXRACCON19KEDN15PC-0568157 | 51QSXRACCON19KEDR07PC-0430346 |  | Off | Defective | Off | 7.8 |  |  | OMNI AEL-2038 |  |  | Working | Off |  | None | None |  | None | CF200 |  | None |  | None | Off |  |  | Off |  | None | INHOUSE A1 | HUAWEI | Off |  | Off | HUAWEI/900 | Off |  | Off |  | Off |  |  | Off | None | HUAWEI 2100/900 | Off |  | Off |  | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM100 | Yes | Trad | Yes | ZTE | ZXMP M721 | Yes | Trad | Yes |  |  | Off | Off | Off | [113 empty] | ELTEK 1 | 53.8 | 1 |  | 8 | 4 | 4 | SACREDSUN |  | SACREDSUN |  | SACREDSUN |  | SACREDSUN |  | Off |  | 53.3 | 53.3 | 53.3 | 53.2 | Off | [18 empty] | 40 | ZTE MAIN | [10 empty] | 20 | XDM100B | [12 empty] | ELTEK | 53.6 | 1 |  | 61 | 4 | 4 | SACREDUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | Off |  | 52.1 | 51.7 | 51.3 | 50.9 | Off | 100 | BTS 3900L UPPER | 100 | DCDU L2100/L850 | 100 | DCDU G2100 |  |  | 63 | DCDU 3G/LTE | 63 | BTS 3900L LOWER | [6 empty] | 40 | BRO PWR | 40 | XDM100 A | 40 | ZTE REDUNDANT | [35 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 25.7 | 70 | ELTEK 1 | 70 | ELTEK 2 | 16 | LIGHT | 20 | SPARE | 32 | ACU 1 | 16 | CO | 32 | ACU 2 | [26 empty] | Done | OK
P40MactanAirport.pdf | P40 | Mactan Airport | 2017-02-07 | Eddie D. Clave Jr. | OK |  | Rectification | For IBS/DAS rehab | OK |  | N/A |  | Off |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A | IBS/DAS | OK |  | OK |  | OK |  | Rectification | Items for pull-out/ARDA | OK |  | OK |  | OK |  | N/A |  | N/A |  | Rectification | For bolt down | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | For floor rehab | Rectification | excess mats for ARDA | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
P65 MACTAN SHANG HOTEL CHECKLIST.pdf | P65 | MACTAN SHANGRILA HOTEL | 2017-03-07 | EDDIE D. CLAVE JR. | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK | WITH IBS | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | Rectification | FOR RELABELLING | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | Rectification | FOR REGROOMING C/O PLDT | N/A |  | N/A |  | N/A |  | Rectification | FOR BATTERY REPLACEMENT AND ADDITIONAL BATTERY PLATES | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | Off |  | Rectification | EXCESS MATERIAL FOR PULL-OUT C/O HUAWEI | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
PMR V3507 Sun Bakilid030617.pdf | V3507 | Sun-Mandaue City-Bakilid | 2017-03-06 | Jerome T. Butong / Ritchie B.Canales | N/A |  | N/A |  | N/A | stolen busbar (outdoor) | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A | all huawei RTN 950(SPDH radio) | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | stolen busbar | OK |  | OK |  | OK |  | N/A | no router | OK |  | OK |  | N/A |  | N/A | no ODF | N/A |  | N/A |  | N/A |  | OK | for additional battery both Eltek and Emerson( sacred sun 180 Ah | OK | 1 bank battery voltage reading 53.6 V(eltek) and 54.2 V at Emerson rectifier (1 bank) | OK |  | OK |  | N/A | no genset | OK |  | OK | stolen busbar | Rectification | porthole for sealant; 1 acu defective for ecall/ checking( not working | Rectification | Excess material from Refarming still on site; broken perimeter wall (for rehab) | OK |  | Percival B. Quijano | B | 42800 | Sacris Road, Bakilid, Mandaue City | Residential | Lot | Permanent | Lot | GT, 120 Ft | Van | 24 hours | Roving Guard | Yes | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | OK | For CSMP Endo | Perimeter wall for rehab ( prone to Theft) | Working | OK | OK | OK | OK | OK | For Rectification | OK | OK | OK | 4 working | OK | Ok | 1 working | OK | For Rectification | For CSMP Endo | there are still many overruns clamps on site | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED M14PC-0532113 | 51QSXRACCON19KED T15PC-0722167 |  | Defective | Working | None | 7.08 A | 7.09 A |  |  |  |  | None | None |  | None | Working |  | Working | CF200 |  | Working | MTR1173949 | None | None |  | TO FOLLOW | For CSMP Endo |  | None |  | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Retrieved | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 900&1800; 3G: U2100; FDLTE: L850 | OK | OK | HUAWEI | HUAWEI RTN950 | Yes | 15159/15187/15243 | 14739/14767/14823 | -0.028561 | OK | Off | Yes | 816 MSC 3 |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | No |  |  |  | Off | Off | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | Off |  |  |  | Off |  | Off | NA | [14 empty] | Yes | Off | Yes |  |  | Yes | Off | Yes |  |  | Yes | Off | No | [40 empty] | Huawei RTN 950 facing MSC3 | S1-P1 | V3507 2G PABIS | S1-P2 | V3507 3G | S1-P3 | V3507 FD-LTE | [66 empty] | ELTEK | 53.99 V | 0.041667 | 21 A | 21 A | 4 | 1 | SACRED SUN | 180 | [6 empty] | No | 1 | 53.6 |  |  |  | OK | 100 |  | 100 |  | 100 | BATTERY | 100 | BATTERY | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 | RTN 950 RDNT FACING 816 MSC 3 | 16 |  | 16 |  |  |  | EMERSON | 54.6 V | 0 | 27.9 A | 27.9 A | 6 | 2 |  |  | SACRED SUN | 180 |  |  |  |  | No |  | 54.2 V |  |  |  | OK | 100 |  | 100 | BAT2 | 100 |  | 100 |  | 16 | RTH 950 MAIN POWER FAC. 816 MSC 3 | 16 |  | 16 |  | 16 |  | 6 |  | 6 |  | 6 |  | 80 | DCDU 1 L850/U2100 | 100 |  | 100 |  | 100 | [30 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 175 | 100 | EMERSON | 30 | ACU 1 | 30 | ACU 2 | 30 | Eltek 2 | 70 | ELTEK 1 | 20 | OB light | 20 | SPARE | 20 | perimeter lights | 20 | C.O | 20 | Alarm System | 15 | LIGHTS | [18 empty] | Done | OK |  | PERCIVAL B. QUIJANO | 42800 | [40 empty] | ACU 1 | defective | 1 | condura
R01 Dan Jose.pdf | R01 | Dan Jose | 2017-03-03 | Eric Brian Aligway | OK |  | N/A |  | Rectification | All grounding and Bus bars are stolen | N/A |  | N/A |  | OK |  | OK |  | OK | Harris facing Talamban for recovery | OK |  | OK |  | OK |  | OK |  | OK | Harris facing Talamban for recovery | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | Rectification | Def. ATS | OK |  | OK |  | Rectification | Def. exhaust fan | OK |  | OK |  |  | B | 42797 | [9 empty] | Off |  | Rogelio Arinasa |  |  |  | Sitio San Jose, Brgy. Talamban Cebu City |  | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
TOC Cell Site PMR (1st Half) 2017_V0077_Umapad.pdf | V0077 | Umapad | 2017-03-02 | Jerome T. Butong / Alan Mark B. Rodrigo | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | All feeder cable clamps need replacement immediately (rusted) | Rectification |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | lacking of modules(not yet used) | OK | Not yet used | N/A |  | N/A |  | OK |  | OK | need replacement of both old rectifier power-one and zte | OK |  | OK |  | OK |  | OK |  | OK |  | OK | to follow tower light, lightning arrester | OK |  | Rectification | Excess material from Refarming still on site | OK |  |  | Off |  | Barangay Umapad, Mandaue City | Residential | Lot | Permanent | Lot | GT, 140 Ft | Van | 24 hours | Caretaker | Yes | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | OK | For CSMP Endo | Gate for rehab(RUSTY) | Defective | OK | OK | For Rehab | OK | OK | OK | OK | None | OK | 3 WO/ 1 Def | OK | Ok | No emergency light | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | 51QSXRACCON19KED E12PC-0257097 | 51QSXRACCON19KED T15PC-0725427 |  | Defective | Working | None | 7.08 A | 7.09 A |  |  |  | 1 working/1 for arda | Defective | Defective | POWERCITY | Working | None | 45 | Working | CF200 | TO FOLLOW | None | MTR1058533 | Working | None | to follow |  | Working | none | Working | Day tank need rehab | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Retrieved | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 900&1800; 3G: 900&2100; FDLTE: 1800, 850 & 2100 | OK | OK | AVIAT | STRATEX | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | XDM 100 | Yes | Off | Yes |  |  | Yes | Off | Yes |  |  | Yes | Off | No |  |  |  | TO FOLLOW | [36 empty] | AVIAT facing MSC3 | S3-P3 | V0077 Umapad 2G Pabis | S3-P4 | V0077 Umapad 3G | S3-P5 | V0077 Umapad FDLTE | [66 empty] | ZTE | 56.9 v | 1.5 A | 8:00 | 45.4 A | 2 | 2 | LYNX | 170 AH | LYNX | 170 AH |  |  |  |  | Yes | 1 | 56.9 v | 56.9 v |  |  | OK | 100 |  | 100 |  | 63 | 2G UPPER/LLVD 1 | 63 |  | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 40 |  | 40 |  |  |  | 80 | BTS 3900L LOWER/LLVD 1 |  | LLVD 2 | 16 | HARRIS B | 16 |  | 16 |  | 16 |  | 6 |  | 6 |  |  |  | Power - One | 54.51 V | -0.4 A | 63.4 A | 64.1 A | 3 | 3 |  |  | RITAR | 150 | RITAR | 150 | RITAR | 150 | No |  |  | 54.51 V | 54.51 V | 54.51 V | OK | 50 |  | 60 |  | 63 |  | 63 | HUAWEI 3G/LTE DCDU | 40 |  | 40 | HUAWEI 3G | 16 | ECI A | 16 | EC B | 16 |  | 10 |  | 10 |  | 10 |  | 10 | HARRIS A | 6 |  | 6 |  | 6 |  | 80 | DCDU-12B G1800 | 80 | DCDU - 12B U900/L850 | [23 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | POWER-ONE | 70 | ZTE AC MAIN | 30 |  | 30 |  | 30 | ACU 1 | 30 | ACU 2 | 20 | LIGHT | 20 | OUTLET | 20 |  | UNREADABLE | TVSS | [20 empty] | Done | OK |  |  |  | GENSET | 1 | POWERCITY 45KVA/G09121296 | c/o WFM | [36 empty] | ACU1 | defective |  | condura
TOC Cell Site PMR Checklist and Inventory Form(1st Half) 2017_5884.pdf | 5884 | Opao | 2017-01-29 | Jerome T. Butong | OK |  | OK |  | OK | As observe on all sites visited, only the cables have grounding not for the antennas | N/A |  | N/A |  | N/A |  | OK |  | N/A | Existing microwave radio is already for dismantling | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK | Lacking one RM for Eltek1 | OK | Both DC power plant have new batteries installed | N/A |  | OK |  | OK |  | OK |  | OK | SNo lifeline installed / No bus bar installed at the middle / Two deadman had no more grounding | OK |  | Rectification | Excess material from Refarming still on site | OK |  |  | Off |  | UC Mandaue Campus,Opao, Manduae City | School | Lot | Permanent | Lot | GT, 150 Ft | Van | 24 hours | Caretaker | Yes | [7 empty] | OK | OK | OK | OK |  | Defective | OK | OK | For Rehab | OK | For Rehab | For Rectification | OK | Expired | OK | ok | OK | Ok | No emergency light | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | T15PC-0741477 | N14PC-0568087 |  | Working | Working | None | 7.21 A | 7.07 A |  |  |  | 1 working | None | None | Powercity | Working | Working | 25 | Working | CF200 | 20.4 | None | 1063269 | Working | None | 100 Liters |  | Working | none | Working | Day tank was not yet installed | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 900&1800; 3G: 900&2100; FDLTE: 700, 850 & 2100 | OK | OK |  |  | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ECI | Apollo | Yes | Off | Yes | ECI | XDM100 | Yes | Off | Yes | Allied Telesis | AT-x610-24Ts/X-POE+ | Yes | Off | No | [41 empty] | Allied P3 | 5884 Opao 2G Pabis | Allied P1 | 5884 Opao 3G | ECI XDM100 I5P9 | 5884 Opao FDLTE | ECI Apollo U0P3 | Allied Telesis Uplink (Port 20) | [64 empty] | ELTEK | 53.65 V | 0 | 38.5 A | 38.5 A | 3 | 2 | Sacred SUN | 180 Ah | Sacred SUN | 180 Ah |  |  |  |  | No |  | 54.4 | 54.4 | 54.4 |  | OK | 80 | Huawei BTS3900L Upper | 80 | Huawei BTS3900L Lower | 100 |  | 100 |  | 63 |  | 63 | ECI XDM100 Source B | 63 |  | 63 |  | 50 |  | 50 |  | 50 |  | 50 |  | 40 |  | 40 | Huawei FDLTE | 40 |  | 40 |  | 16 | ECI Apollo Source A | 16 |  | 16 |  | 16 |  | 6 |  | 6 |  | ELTEK | 54.21 | 0 | 30.6 A | 30.6 A | 4 | 3 | Sacred SUN | 180 | Sacred SUN | 180 |  |  |  |  | No |  | 53.4 V | 53.4 V |  |  | OK | 100 | DCDU A | 100 | DCDU B | 100 | DCDU C | 100 |  | 63 | ECI XDM100 Source B | 63 | ECI Apollo Source B | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 | Allied Turbo Switch | 20 |  | 16 |  | 16 |  | 16 |  | 16 | Allied Turbo Switch | [15 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 70 | ELTEK1 SourceA | 70 | ELTEK1 Source B | 40 | ELTEK2 Source A | 40 | ELTEK2 Source B | 40 | ACU 1 | 40 | ACU 2 | 32 | Perimeter Light | 32 |  | 32 | Lighting | 32 | C.O. | [20 empty] | Done | OK |  |  |  | WACU | 2 | Condura 2HP | c/o WFM
TOC Cell Site PMR Checklist and Inventory Form(1st Half) 2017_872.pdf | 872 | Tabok | 2017-02-10 | Jerome T. Butong | OK |  | OK |  | OK | As observe on all sites visited, only the cables have grounding not for the antennas | N/A |  | N/A |  | OK |  | OK |  | N/A | No microwave radio installed | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | No surge suppressor installed | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK | Lacking one RM for Eltek1 | OK | Both DC power plant have new batteries installed | N/A |  | OK |  | OK |  | OK |  | OK | No lifeline installed / No bus bar installed at the middle / All dead man had no more grounding | Rectification | For rectification by re-farming contractor | Rectification | Excess material from Refarming still on site | OK |  |  | Off |  | Tingub, Manduae City | Residential | Lot | Permanent | Lot | GT, 150 Ft | Van | 24 hours | Caretaker | Yes | [7 empty] | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | For Rehab | OK | For Rehab | For Rectification | OK | Expired | OK | ok | OK | Ok | No emergency light | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONA019ED | WCONX019ED1 |  | A12PC-0041138 | B15PC-0154353 |  | Working | Working | None | 7.08 A | 7.09 A |  |  |  | 1 working | None | None | Denyo | Working | None | 25 | Working | CF200 | 2053.8 | None | 1035713 | Working | None | 100 Liters |  | Working | none | Working | Day tank was not yet installed | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | Off | Boser | 6 | Retrieved | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 900&1800; 3G: 900&2100; FDLTE: 1800, 850 & 2100 | OK | OK |  |  | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | Off | Off | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | No |  |  |  | OK | OK | Yes |  |  |  | Off |  |  |  | Off |  | Off | [13 empty] | ZTE | OTN721-M20150700171 | Yes | Off | Yes | ECI | XDM100 | Yes | Off | Yes |  |  | Yes | Off | No | [41 empty] | ECI I5-13 | 872 Tabok 2G Pabis | ZTE 0/0/10 - C1 | 872 Tabok 3G | ZTE 0/0/9 - C1 | 872 Tabok FDLTE (Tempo@ ECI I5-11) | ECI I5-9 | 872 Tabok BRO Canopy | [64 empty] | ELTEK | 54.2 V | 0 | 45.4 A | 45.4 A | 3 | 2 | Sacred SUN | 180 Ah | Sacred SUN | 180 Ah |  |  |  |  | No |  | 54.2 | 54.2 |  |  | OK | 100 | CNS B Failsafe | 100 |  | 50 |  | 50 | DCDU 3 | 32 |  | 32 | ZTE FS REDUNDANT | 32 |  | 32 |  | 32 |  | 16 | ECI SOURCE B | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 10 |  | 10 |  | 80 | Huawei BTS3900L Lower | 6 |  | 6 | 3G 850 RRU sec1 (breaker 23) | 6 | 3G 850 RRU sec2 (breaker 24) | 6 | 3G 850 RRU sec3 (breaker 25) | ELTEK | 53.87 | 0 | 43.0 A | 43.0 A | 4 | 4 | Sacred SUN | 180 | Sacred SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.8 V | 53.8 V | 53.8 V | 53.8 V | OK | 100 | BTS 3900L UPPER | 100 | CNS A FAILSAFE | 100 | DCDU 1 | 100 | DCDU 2 | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | ECI SOURCE A | 40 | ZTE FS MAIN | 40 |  | 40 |  | 40 |  | 40 |  | 20 |  | 20 |  | 20 |  | 16 |  | 16 |  | 16 |  | 16 | [16 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK2 Source A | 40 | ACU 1 |  |  | 30 | OPTO 22 |  |  | 30 |  | 20 | C.O. | 20 | CABIN LIGHT | 40 | TOWER LIGHT | 70 | ACU 2 | 70 | ELTEK 1 | 50 | ELTEK2 Source B | 40 | P-LIGHT | 40 | [13 empty] | Done | OK |  |  |  | DC POWER PLANT | 1 | EMPOWER | c/o WFM | BATTERIES | 12 | RITAR
TOC Cell Site PMR Checklist and Inventory Form(1st Half) 2017_F67_Looc.pdf | F67 | Looc | 2017-01-25 | Jerome T. Butong | OK | 0357 coor number | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | mounting bracket already very rusty. Need immediate rectification. | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | Rectification | Needs electrical upgrade | N/A |  | OK |  | Rectification | Tower loading for evaluation. WATO observe that tower loading beyond its capacity | OK |  | N/A |  | OK |  |  | B |  | Rm 301 Rock XII Bldg., Mabini St., Looc, Mandaue City | Commercial | Room 301 | Permanent | Building | Guyed 50ft | Room | 8am-5pm | Admin/Bldg Security | Yes | [7 empty] | Off | Off | Off | Off |  | Defective | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | N/A | Off | Boser | 6 | Retrieved | Off | BTS3900 | Retrieved | BTS3900 | Retrieved | N/A | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [45 empty] | 150 |  |  | 70 | ELTEK 2A |  |  | 70 | ELTEK 1A |  |  | 40 | ELTEK 2B |  |  | 40 | ACU 1 |  |  | 20 |  |  |  | 20 |  |  |  | 30 | ACU 2 |  |  | 20 | ELTEK 1B | [8 empty] | Off | Off
TOC Cell Site PMR Checklist and Inventory Form(1st Half) 2017_V3716.pdf | V3716 | SUN Mandaue Casuntingan 2 | 2017-01-26 | Jerome T. Butong | OK | Coordinating #: Q1-0383 | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | Off |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | Eltek rectifier was no installed controller since i resume site ownership | OK | Both DC power plant have new batteries installed | N/A |  | OK |  | Rectification |  | OK |  | OK | Some MW mounting bracket needs repainting / No lifeline installed / No bus bar installed at the middle | OK |  | Rectification | Gate need repair / Excess material from Refarming still on site | OK |  |  | Off |  | Ceniza Property, M.L. Quezon St.,Casuntingan, Manduae City | Residential | Lot | Permanent | Lot | SST, 150 Ft | Van | 24 hours | Caretaker | Yes | [7 empty] | For Repair | OK | for Replacement | OK |  | Defective | For Rectification | OK | For Rehab | OK | OK | For Rectification | OK | Expired | OK | ok | OK | Off | No emergency light | OK | Off | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 |  | T15PC-0741943 | F15PC-0370765 |  | Working | Off | None | 7.08 A | 7.16 A |  |  |  | 1 Def | None | None | Weichai | Defective | Working | 28 | Working | CF200 |  | None | 10672810 | Working | None | 100 Liters |  | For CSMP Endo | none | Working |  | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved |  | Off |  | Off |  |  | Off | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 900&1800; 3G: 900&2100; FDLTE: 850 | OK | OK | Huawei | RTN950 | No |  |  |  | OK | OK | Yes | 816 MSC3 | Huawei | RTN950 | No |  |  |  | OK | OK | Yes | 4305 Cabancalan Warehouse | Huawei | RTN950 | No |  |  |  | OK | OK | Yes | V3703 SUN Cabancalan | Huawei | RTN950 | No |  |  |  | OK | OK | Yes | V3473 SUN Tawason | Huawei | RTN950 | No |  |  |  | OK | OK | Yes | V3504 SUN Mandaue Casuntingan 1 |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | S1P2 facing 4305 | V3716 SUN Casuntingan2 2G | S1P3 facing 4305 | V3716 SUN Casuntingan2 3G | S1P2 facing MSC3 | V3716 SUN Casuntingan2 FDLTE | S1P4 facing 4305 | Allied Turbo Switch NMS | [13 empty] | 2G/3G | S1P1 facing 4305 to S1P1 facing V3703 | 2G/3G/FDLTE | S1P1 facing V3504 to S1P2 facing V3703 | 3G/FDLTE | S1P4 facing V3504 to S1P3 facing 816 | 2G/3G/FDLTE | S1P1 facing V3473 to S1P1 facing 816 | [43 empty] | Emerson | 54.8 V | 0 | 34.1 A | 34.1 A | 8 | 3 | Sacred SUN | 150 Ah | Sacred SUN | 150 Ah | Sacred SUN | 150 Ah |  |  | No |  | 54.4 | 54.4 | 54.4 |  | OK | 16 | Huawei RTN950 facing V3703 Main | 16 | Huawei RTN950 facing 4305 Main | 16 | Huawei RTN950 facing V3473 Redundant | 16 | Huawei RTN950 facing V3504 Redundant | 6 |  | 6 |  | 6 |  | 50 |  | 16 | Huawei RTN950 facing 816 Main | 63 | WCDMA DCDU-12B | [24 empty] | ELTEK |  |  |  |  | 4 | 2 | Sacred SUN | 180 | Sacred SUN | 180 |  |  |  |  | No |  | 53.4 V | 53.4 V |  |  | For Rectification | 100 | DC Distribution Center | 100 | DCDU G900/L850 | 100 | DCDU G1800 | 100 |  | 63 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 40 |  | 20 | Huawei RTN950 facing 816 Redundant | 20 | Allied Turbo Switch | 20 |  | 16 | Huawei RTN950 facing V3703 Redundant | 16 | Huawei RTN950 facing V3504 Main | 16 | Huawei RTN950 facing 4305 Redundant | 16 | Huawei RTN950 facing V3473 Main | [15 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 100 | Emerson Rectifier | 30 | Lighting | 20 | AC outlet | 30 | ACU2 | 20 |  | 20 | OB Light | 20 | Perimeter Lights | 20 | Eltek Redundant | 20 | ACU 1 | 20 |  | 20 | ACU controller | 20 |  |  |  | 70 | Eltek Main | [12 empty] | Done | OK | No controller installed on ELTEK rectifier |  |  | Batteries | 8 | Acme 100Ah Batteries | c/o WFM
V0026 ANTIPOLO RS - 03282017.pdf | V0026 | Antipolo RS | 2017-03-28 | Jerome Butong | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | for labeling | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | SST-150 | VAN | 24HRS | CARETAKER | Off | [6 empty] | N/A | N/A | N/A | N/A | For CSMP Endo |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | Off | 2/4 | OK | Off | N/A | Off | Off | Off |  | WACU | WACU | Off | CONDURA/WCONX019E01 | CONDURA/FP-51QSXRACCONR19KEDP1C |  | 51QSXRACCON19KEDT15PC-0722298 | 51QSXRACCON19KEDN10PC-0470216 |  | Working | Working | Off | [5 empty] | 42736 | Off | Off | DENYO | Defective | Working | 25 | Working | CF200 | DEFECTIVE | None |  | Working | None | 200 LITERS |  | Working | N/A | Working |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | HARRIS | STRATEX | Yes | 7513 ; 7777.350; 7836.650 | 7681 ; 8088.670; 8147.970 | -42/-47 ; -42 ; -43.50 | OK | OK | Yes | PLDT TUBURAN | HARRIS | STRATEX | Yes | 7149; 7807 | 7345; 8118.32 | -32/-36 ; -40/-40.20/ | OK | OK | Yes | ASTURIAS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | FACING ASTURIAS | S7 P5 | ANTIPOLO RS 2G 2ND E1 | S7 P13 | ANTIPOLO RS 2G 1ST E1 | [34 empty] | AVIAT FACING ASTURIAS | S3 P2 | ANTIPOLO RS 3G | S6 P2 | PLDT TUBURAN 3G | S6 P3 | BANTAYAN/TUBURANTP/TABUELAN | S3 P3 | BANTAYAN BRO CLUSTER | [12 empty] | AVIAT FACING PLDT TUBURAN | S3 P2 | PLDT TUBURAN 3G | S3 P3 | BANTAYAN BRO CLUSTER | S6 P3 | BANTAYAN/TUBURANTP/TABUELAN | [45 empty] | ELTEK | DEFECTIVE |  |  | DEFECTIVE | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 53.3 | 53.3 | 53.3 | 53.3 | Off | [40 empty] | 16 | FMS | 16 | FMS | EMERSON | 54.5 | FLICKERING |  | 28 | 3 | 2 | SACREDSUN | 180 | SACREDSUN | 180 |  |  |  |  | Off |  | 53.2 | 53 |  |  | Off |  |  |  |  | 63 | DCDU 3G | 63 | BTS3900L LOWER | 40 | DCPDB B | [20 empty] | 6 | FMS | 80 | BTS3900L UPPER | [10 empty] | ZTE | 54.3 |  |  | 5 | 3 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | Off | [5 empty] | Off | [20 empty] | 40 | DCPDB A | [22 empty] | 100 | 18.32 | 70 | ZTE RECTIFIER | 70 | POWERONE | 50 | ELTEK 2 | 50 |  | 40 | SPARE | 40 | ELTEK 1 | 40 | TVSS | 40 |  | 30 |  | 30 |  | 30 |  | 30 |  | 20 |  | 20 | [13 empty] | Done | OK | EXCESS MATERIALS/ 3 BANKS LEOCH FOR ARDAMICROWAVE ANTENNA FOR ARDA/ACU FOR ARDA/ELECTRICAL POST FOR REPLACEMENT. 17Q1-1883
v0072-Peace Valley-012317.pdf | V0072 | Peace Valley | 2017-01-23 | Lemuel Balbuena | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK | for tower loading re-calculation | OK |  | OK |  | OK |  |  | B |  |  | Commercial | 2nd Floor Rooom | Permanent | Building | Monopole 30FT | Van | 8am-5pm | Roving Guard | Yes | [6 empty] | n/a | N/A | N/A | N/A | Off | Building Site | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | working | OK | For Rectification | Off |  | WACU | Off | Off |  |  |  | J12PC-03277233 |  |  | Working | Off | Off | 8.2 |  |  | Standard |  |  | Working | Off | n/a | None | None | n/a | None | Off | n/a | None |  | None | None | n/a |  | Off |  | Off |  | Huawei | Retrieved | huawei | Off | Huawei | Off | Huawei | Off | Huawei | Off | Boser | 6 | Retrieved | Off | Huawei | Retrieved |  | Off | n/a | Off |  | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [113 empty] | PowerOne | 54.5 | 0 | 74 | 74 | 4 | 3 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 |  |  | No |  | 50.4 | 54.2 | 54.2 |  | OK | 100 | BATTERY BANK | 100 | BATTERY BANK | 100 | BATTERY BANK | 80 | L700 |  |  |  |  | 63 | HUAWEI DCDU LTE/U2100 |  |  | 80 | DCDU 1 G1800 | 16 | XDM100 POWER A | 16 | XDM100 POWER B |  |  | 10 | ECI 4B RAP SOURCE A | 10 | CMM ROUTER BREAKER | 10 | ECI 4B RAP SOURCE B | 10 | BRO ROUTER |  |  | 80 | DCDU 2 L850 U21 | 80 | BTS3900L UPPER | 80 | BTS3900L LOWER | [19 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 29.4 | 70 | POWERONE | 20 |  | 70 |  | 20 | C.O | 50 |  | 30 | LIGHTS | 50 |  | 30 |  | 40 |  | 40 |  | 40 | ACU2 | 40 | ACU 1 | [16 empty] | Done | OK | excess materials onsite,bts cabinet for arda,ceiling for cover |  |  | HUAWEI CABINET | 1 | with 3 wrfu | WATO | Koppel ACu | 1 |  | WFM | [117 empty] | tower for tower loading review | [5 empty] | for arda
V0086 CASILI HILLS PMR V2.pdf | V0866 | Casili Hills | 2017-01-13 | Albert Ambil/Greggy Vale | OK | VSWR ranges from 1.1 to 1.2 | N/A |  | Rectification | Tower grounding for rehab | N/A |  | OK | Bro GPS ok. | OK | ok. | OK |  | OK |  | N/A | no SPDH. | OK |  | OK |  | OK | Ok done back-up for 3G and LTE. | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | Rectification | 2 RM defective w/ SPMS already requested, 52.65V. | Off |  | OK |  | OK |  | OK | ATS for replacement, genset for repair. | OK |  | OK | No outdoor busbar | Rectification | Van ceiling for rehab. | OK |  | OK | ok, taken by A. Ambil. | Percival Quijano | A | 42748 | Demetrio Cortes Cmpd, Brgy. Cubacub, Mandaue City | A | at lot | Tap to neigbor | Lot | SST 32m | concrete | 24 | via SV | Yes |  | Demetri Cortes |  |  |  | Cubacub, Mandaue City | working | N/A | N/A | OK | OK | No gate and perimeter | Working | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | working | OK | Ok | None | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 | NA | 51QSXRACCON19KED F15PC-0370724 | 51QSXRACCON19KED T15PC-0756891 | NA | Working | Working | None | 7 | 7 |  |  |  | DEFECTIVE STARTER | None | None | KIPOR | Defective | None | 45 | None | CF200 | 1549.03 | None | 2006-09016247 | Working | None | 600L | 2006-09016247 | For CSMP Endo | NONE | Working | TAP TO NEIGHBOR | BTS3900L | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off | BOSER | 2 | Retrieved | None | BTS3900 | Retrieved |  | Off |  | Off | OK. | OK | OK |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | i1-1 | V0086 2G | [109 empty] | Eltek | 54.05V | 0 | 71 | 71 | 4 | 3 | Sacred SUN | 180 | Sacred SUN | 180 | Sacred SUN | 180 |  |  | No | NA | 53.8 | 53.94 | 53.01 |  | OK | 100 | BTS3900L UPPER | 100 | BTS3900L LOWER | 100 | DCDU 1 U2100 G900 | 100 | DCDU2 L850 | [10 empty] | 40 | ECI SOURCE A | 40 | ECI SOURCE B | 40 | 3G LTE DCDU | 40 | ZTE FS MAIN | 40 | ZTE FS REDUNDANT | [10 empty] | 16 | DC-DC 24V | 16 | SWITCH | 16 | ROUTER | [15 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off |  | PERCIVAL QUIJANO | 42748 | NOKIA RECTIFIER | 1 | NOKIA RECTIFIER SN: 663094 | WFM | CONDURA ACU | 1 | WINDOW SN: 51QSXRACCON19KED07PC-0054642 | WFM
V0684 SU CEBU DOCTORS UNIVERSITY-02172017.pdf | V0684 | SUN CEBU DOCTOR UNIVERSITY | 2017-02-17 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK | ELTEK RECTIFIER NO BATTERY TERMINAL | OK |  | OK |  | Off |  | N/A |  | OK |  | OK |  | Off |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | BUILDING | POLE | VAN | 8AM-5PM | ROVING GUARD | Off | [6 empty] | N/A | Off | Off | Off | Off | BUILDING SITE | Off | OK | OK | Off | OK | OK | OK | OK | OK | OK | 0/4 | OK | Ok | DEFECTIVE | OK | OK | For CSMP Endo |  | WACU | WACU | Off | CONDURA | PANASONIC |  | N14PC-'0558040 | J12PC-'0377140 |  | Working | Defective | Off | 8.2 |  |  | SPECTRUM |  |  | Defective | Off |  | None | None |  | None | Off |  | Working |  | Off | Off |  |  | Off |  | Off |  | HUAWEI | Retrieved |  | Off | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | NORTH RECLAIMATION |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 2G | 3 | 3G | [68 empty] | EMERSON | 54.6 |  |  | 28 | 3 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | No |  | 53.3 | 52.9 | 52.6 |  | OK | [44 empty] | ELTEK | 53.93 |  |  |  | 4 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 8 | 100 | RECTIFIER | 30 | ACU 1 | 20 | C.O | 30 | ACU 2 | 15 | E.LIGHTS | 30 | ACU 3 | 15 | OBLPC | 20 | ELTEK 2 | 20 | SPARE | 70 | ELTEK 1 | [20 empty] | Done | OK
V0855 Binongkalan.pdf | V0855 | Binongkalan | 2017-02-08 | G. VALE | OK | All are 1.1. | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | DONE 3G only. | OK | -38/-39 dBm. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | no bro. | N/A |  | OK |  | OK |  | OK |  | N/A | NO ODF. | N/A |  | N/A |  | N/A | NO BRO. | OK | NO BRO. | OK | ABOUT 3 HOURS BACK-UP. | OK |  | Off |  | OK | genset cant set to auto. | OK |  | OK |  | OK |  | Rectification | Need grass-cutting. | OK |  | PERCIVAL QUIJANO | A | 2017-02-28 | BRGY. BINONGKALAN, CATMON, CEBU | RESIDENTIAL | LOT | PERMANENT | LOT | SST 3 LEGGED | VAN | 24H | CARETAKER | Yes | 2018 | UNKNOWN | UNKNOWN | 124.0275 | 10.633 | UNKNOWN | 4, 0 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 8, 0 | OK | Ok | 1, 0 | OK | OK | OK |  | WACU | WACU | WACU | WCONR019ED | WCONH019ED | FP-51QSXRACCONR19KEDP1C | 141702892 | 51QSXRACCON19KED K16PC-1074154 | 51QSXRACCON19KEDR08PC-0751178 | Defective | Defective | Working | 0 | 8 | 0 | ASAHI | ASAHI | 1, 0 | Defective | Defective | DENYO | Working | Working | 25 | Working | CF200 | 5153 | Working | 316069 | Working | None | 150 | 2BMNM355201 | Working | 0 | Working | DENYO SN: 5402434, NOTE: Genset unable to set to AUTO mode. ATS is not defective. Genset works via manual operations. ATS: PowerCity SN: 15030690 | BTS3900 | Retrieved | BTS3900 | Retrieved | none | Off | BTS3900 | Retrieved | NONE | Off | NONE | 0 | Off | Off | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | FUJITSU | FRX | Yes | 8183.32/8177.62/8059.02 | 7807/7866.3/7747.70 | -0.024948 | OK | OK | Yes | 812 CATMON | FUJITSU | FRX | Yes | 6880/6800/6960 | 6540/6620/6460 | -0.024948 | OK | OK | Yes | 805 DANAO | HUAWEI | RTN980 | Yes | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | Yes | 812 CATMON | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | XDM-100 | Yes | Trad | Yes | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  | EC-XDM100 | i1-1 | V0855 2G 1ST E1 | i1-2 | V0855 2G 2ND E1 | i3-3 | RTN980 NMS | [6 empty] | RTN980 FACING 812 CATMON |  | NONE | [23 empty] | ECI XDM-100 | i5-2 | V0855 BINONGKALAN 3G | [20 empty] | NONE | [19 empty] | NONE | [29 empty] | ELTEK | 53.95 | 0 | 16 | 16 | 3 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | No |  | 51.5 | 51.8 | 51.9 | N/A | OK | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 80 | RTN980 FACING 812 CATMON | 80 | SPARE | 80 | SPARE | 80 | SPARE | 63 | FUJITSU DCPDB DANAO BLOCK A | 63 | FUJITSU DCPDB CATMON BLOCK A | 63 | SPARE | 63 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | HUAWEI 3G 850 | 20 | SPARE | 20 | SPARE | 20 | FMS (OFF) | 20 | SPARE | 10 | SPARE | 10 | SPARE | ELTEK | 54.34 | 0 | 32 | 32 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | No |  | 51.9 | 51.9 | 51.9 | N/A | OK | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 80 | HUAWEI BTS3900 LOWER | 80 | HUAWEI BTS3900 UPPER | 80 | SPARE | 80 | SPARE | 63 | FUJITSU DCPDB DANAO BLOCK B | 63 | FUJITSU DCPDB CATMON BLOCK B | 63 | SPARE | 63 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SCC J18 (OFF) FMS | 20 | SPARE | 10 | SPARE | 10 | SPARE | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 70 | ELTEK RS | 70 | ELTEK RS | 30 | ACU2 | 70 | ELTEK 1 | 30 | ACU1 | 30 | ACU3 | 30 | ELTEK 2 | 30 | OL | 30 | SPARE | 20 | LT | 20 | LIGHT | 20 | SPARE | [16 empty] | Done | OK | ELTEK1 SN:104324100350 ELTEK2 SN: 114524100927 | PERCIVAL QUIJANO | 2017-02-28 | SUPPORT | 1 | POWERONE SN: UNREADABLE | WFM | SUPPORT | 1 | KUTAI SN: 8879 | WFM | [32 empty] | SUPPORT | GENSET |  | DENYO |  | 25 | UNABLE TO SET AUTO | SUPPORT | ELTEK RECTIFIER |  |  |  |  | MISSING 1 RM
V0874SUNLapulapu002.pdf | V0874 | SUN - Lapu-Lapu_002 | 2017-03-20 | Astrobal A. Trozo | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | excess materials for pull out; main gate for rehab; this site is for decommission | OK |  | PERCIVAL B. QUIJANO | B | 42814 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V0907 SM Consolacion1.pdf | V0907 | SM Consolacion1 | 2017-02-16 | A. Ambil | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A | INDOOR SITE | OK |  | N/A |  | OK |  | PERCIVAL QUIJANO | A | 2017-02-16 | SM Consolacion admin, SM City Consoalcion, Consolacion, Cebu | Commercial | Cinema | SUBMETER | Building | N/a | ROOM | Mall hours | Admin | Yes |  | SM Consolacion | N/A |  |  | SM Consolacion | N/A | N/A | N/A | OK | For CSMP Endo | INDOOR SITE | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4, 0 | OK | Ok | 0, 1 | OK | OK | OK |  | Split Type | Split Type | Off | 42LUC022308/CARRIER | CARRIER UNKNOWN |  | UNREADABLE | UNREADABLE |  | Working | Working | None | 15 | 15 |  |  |  | 0, 0 | None | None | N/A | None | Working | N/A | None | Off | N/A | None | N/A | None | None | N/A | N/A | Off | N/A | None |  | BTS3900 | Retrieved |  | Off | BTS3900 | Retrieved | NONE | Off | NONE | Off | NONE |  | Off | Off | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | NONE |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE | [11 empty] | ECI | XDM-100 | Yes | Trad | Yes | ZTE | ZXMP M721 | Yes | Trad | Yes |  |  | Off | Off | Off |  | XDM-100 | i1-1 | v0907 2g 1st e1 | [36 empty] | zte fs | slot10- c2 opt | V0907 3G VIA ZTE FS | [39 empty] | 48F OSP1 CORE 3/4 | FACING F50 CONSOLACION2 |  | 48F OSP2 CORE 1/2 | FACING V5128 SM LACION2 |  | 48F CORE 1/2 | FACING SMARTSTORE | [23 empty] | ELTEK | 54.72 V | 0 | 27 | 27 | 4 | 2 | LYNX | 170 | LYNX | 170 | NONE | NONE | NONE | NONE | No |  | 49.5 | 49.8 |  |  | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 80 | SPARE | 80 | SPARE | 80 | SPARE | 80 | V0907 2G/3G | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | SOURCE A ECI XDM-100 | 40 | ZTE FS MAIN | 40 | ZTE FS REDUNDDANT | 40 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SPARE | 10 | SPARE | 10 | SPARE |  |  | ELTEK | 54.36 | 0 | 0 | 0 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.5 | 53.5 | 53.5 | 53.5 | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 80 | SPARE | 80 | SPARE | 80 | SPARE | 80 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | [15 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK1 | 70 | ELTEK2 | 30 | ACU1 | 30 | ACU2 | 20 | EMERGENCY LIGHT | 20 | LIGHTINGS | 70 | ELTEK NEW 1 | 20 | OULTLET |  |  | 20 | SPARE | [20 empty] | Done | OK | ELTEK SN1: 120124100280 ELTEK SN2: 150924000098 | PERCIVAL QUIJANO | 2017-02-16
V0917 Sun Lapulapu City Mactan 3.pdf | V0917 | Sun Lapu-lapu City | 2017-01-24 | EDDIE D. CLAVE JR | OK |  | OK |  | Rectification | No outdoor busbar | N/A |  | N/A | No Bro/Wimax | N/A | No Bro/Wimax | OK |  | OK |  | OK |  | N/A | No Bro/Wimax | OK |  | OK |  | OK |  | Rectification | For re-label of some equipments | OK |  | Rectification | No outdoor busbar | Rectification | For re-grooming/recovery of decommissioned equipment | Rectification | For re-grooming/recovery of decommissioned equipment | N/A | No Bro | N/A | No Bro | OK |  | OK |  | N/A | No Mux | N/A | No ODF | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | Defective ATS. | N/A |  | OK |  | Rectification | Port Hole for Sealant. For re-checking of van leaks | Rectification | Unclean surrounding. Materials for pull-out/ARDA | OK |  |  | B | 2017-01-24 | Brgy. Mactan 3, Lapu-lapu City Cebu | Commercial | Lot | Permanent | Lot | SST | Van | 24hrs | Caretaker | Yes | August 31,2013 |  |  | 124-00-10.15 | 10-18-06.8 |  | 2017-04-01 | OK | OK | OK | For CSMP Endo | For cleaning | Working | OK | OK | For Rehab | For Grooming | For Rehab | For Rectification | OK | OK | OK | 2017-02-02 | For Rectification | For Rehab | 0/0 | For Tagging | For Rectification | For CSMP Endo | for van cleaning; ant infestation | WACU | WACU | Off | FP-51QSXRACCON19KEAC | WCONX019EA1 |  | 51QSXRACCONKEAC10PC-0203668 | 51qSXRACCON19KEAK12PC-095731 |  | Working | Working | None | [5 empty] | 2000-01-01 | None | None | Weichai | Defective | Working | 37.5 | None | Off | 1.74 | Working |  | Working | None | 17 inches of 1000L |  | Working | 0 | Working |  | BBU3900 | Retrieved | BBU3900 | Retrieved | BBU3900 | Retrieved |  | Off |  | Off |  |  | Off | None |  | Off |  | Off |  | Off |  | Off | Off | Huawei | RTN980L | Yes |  |  |  | OK | Off | Yes | Sun LLC Pajac1 | Huawei | RTN950 | Yes | 13045/ 13101 | 12779/ 12835 | 0.98638 | OK | OK | Yes | 873 Maribago | Huawei | RTN950 | Yes |  |  |  | OK | Off | Yes | V3599 Sun LLC Punta Engano 2 | Huawei | RTN950 | No | 12765 | 13031 | -34.4 | OK | OK | Yes | V3494 Sun LLC Agus |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | N/A | [14 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | No Line Driver | [112 empty] | Emerson | 54.8 | 0 | 14.2 | 14.2 | 6 | 4 | Acme | 100 | Acme | 100 | Acme | 100 | Acme | 100 | Yes | 2,3,4 | 54.68 | 54.75 | 54.76 | 52.06 | OK | [8 empty] | 32 | RTN980L Redundant facing LLC Pajac1 | 16 | RTN950 Main facing V3599 |  |  | 16 | RTN950 Main facing 873 | 6 | RTN950 Redundant facing V3494 | [26 empty] | Eltek | 54.55 | 0 | 74 | 74 | 4 | 4 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | Sacred Sun | 180 | No |  | 54.55 | 54.55 | 54.55 | 54.55 | OK | 100 | Red | 100 | Yellow | 100 | Green |  |  | 63 | BTS3900 | [8 empty] | 40 | V0917 3g Turbo | 40 | RTN980L Main facing Sun LLC Pajac1 | [6 empty] | 40 | RTN NodeB |  |  |  |  | 20 | FMS |  |  | 16 | RTN950 Main facing V3494 | 16 | RTN950 Redundant facing V3599 | 16 | RTN950 Redundant facing 873 | [15 empty] | Off | [5 empty] | Off | [44 empty] | 175 |  | 100 | Emerson Rectifier | 20 | van light | 20 | C.O | 30 | WACU 1 | 30 | WACU2 | 20 | OB light | 20 | Perimeter Light | 20 | FAS | 70 | Eltek 1 | 20 | Spare | 70 | Eltek 2 | 20 | Spare | [16 empty] | Done | OK |  |  | 2017-01-24 | Huawei BTS3900A | 1 |  | Build | 2 RTN620 | 2 | 98OHH080191-001/ 98OHH080335-002 | TPE | Huawei BBU3900 | 1 | 210231584810A109991 | RF | Acme 100AH | 4 | N/A | WFM | Ericsson Minilink | 1 | T061607276 | TPE
V3444 Sun Bankal.pdf | V3444 | Sun Lapu-lapu City Pajak 1 | 2017-03-15 |  | Off |  | OK |  | Rectification | stolen grounding busbars | N/A |  | N/A |  | OK |  | N/A | rru on top(no feeder cable) | OK |  | OK |  | N/A |  | OK |  | Off |  | Off |  | Off |  | Off |  | Rectification | stolen grounding busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | defective 2 banks ritar 150ah | Rectification | eltek 0 back-up | OK |  | OK |  | Rectification | genset wont start | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | need major grass cutting | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3445 SUN-LLC-BASAK.pdf | V3445 | SUN - Lapu-Lapu City-Basak | 2017-03-15 | Astrobal A. Trozo | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | main gate for repainting and rehab; excess mats for pull out | OK |  | PERCIVAL B. QUIJANO | B | 42809 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
v3446 Sun-LLC-Marigondon 1.pdf | V3446 | SUN-Lapu-Lapu City-Marigondon 1 | 2017-03-16 | Astrobal A. Trozo/Ritchie B. Canales | OK |  | N/A |  | N/A | Stolen outdoor busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | for external alarms simulation c/o huawei | N/A | stolen outdoor busbar | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | for external alarms rectification c/o huawei; emerson rectifier and battery for replacement | OK |  | OK |  | OK |  | N/A | no genset | OK |  | OK |  | OK |  | N/A | excess mats for pull out; 2 defective perimeter light | OK |  | PERCIVAL B. QUIJANO | B | 42810 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3448-SUN CEBU CITY LAHUG 1-02152017.pdf | V3448 | SUN CEBU CITY LAHUG 1 | 2017-02-15 | LEMUEL BALBUENA | OK |  | N/A |  | Rectification | STOLEN OUTSIDE GROUNDING | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | 4-SST 150FT | VAN | 24HRS | ROVING GUARD | Yes | [6 empty] | WORKING | OK | OK | OK | For CSMP Endo | FOR GRASS CUTTING | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2000-02-01 | OK | Ok | N/A | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CONDURA/WCONX019ED1 |  | 51QSXRACCON19KEDK15PC-0526490 | 51QSXRACCON19KEDK15PC-0540067 |  | Working | Working | Off | 8.2 | 8.1 |  |  |  |  | None | Off |  | None | Working |  | None | Off |  | Working |  | Off | Off |  |  | Off |  | Off | INHOUSEA1 | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Off |  | Off |  | Off |  |  | Off | None | HUAWEI | Retrieved |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | 829 LAHUG |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | RTN 950 EG4 | 1 | 2G | 2 | LTE | 3 | 3G | [66 empty] | ELTEK | 54.18 |  |  | 28 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 53.2 | 53.1 | 53 | 52.9 | OK |  |  |  |  | 100 | DCDU UPPER G1800/900 | [10 empty] | 63 | nodeb | [14 empty] | 20 | RTN 950 FACING 829 LAHUG MAIN |  |  | 16 | rtn dcpdb | [6 empty] | EMERSON | 53.5 |  |  | 23 | 4 | 4 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | Off |  | 51.5 | 51.9 | 51.1 | 51 | Off | [6 empty] | 40 | RTN 950 FACING 829 LAHUG REDUNDANT | 40 | WCDMA DCDU | 100 | DCDU LOWER L850 | [47 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 20.1 | 70 | EMERSON RECTIFIER | 32 | ACU 1 STACU | 20 | C.O | 32 | ACU 2 STACU | 20 | CABIN LIGHTS | 20 | O.B LIGHT | 20 | ALARM | 20 | ELTEK 1 | 20 | PERIMETER LIGHTS | 20 | ELTEK 2 | [20 empty] | Done | OK | AREA FOR GRASS CUTTING,2G RECOVERED MATERIALS FOR ARDA C/O BUILD, NO PERIMETER LIGHTS, NO TOWER LIGHT, STACU FOR CHECKING
V3451SUNBABAG.pdf | V3451 | SUN-Lapu-Lapu City-Babag | 2017-02-18 | Astrobal A. Trozo | OK |  | N/A | no diplexers, trixplexers and combiners | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | waiting for IT for huawei software installation | N/A | waiting for IT for huawei software installation | OK |  | Rectification | for rectification of external alarms | OK |  | OK |  | OK |  | OK |  | N/A | no CMM/Router | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | excess materials for pull out; vehicular gate chain and padlock for replacement and repainting of gate ;1 acu for arda(carrier) | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
v3454-SUN CATMON FLORES-01142017.pdf | V3454 | Sun Catmon Flores | 2017-01-24 | Lemuel Balbuena | OK |  | N/A |  | Rectification | stolen outside busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | ats manual | OK |  | OK |  | OK |  | OK |  | OK |  |  | B |  | Flores (Pob.), Catmon, Cebu | Commercial | Lot | Permanent | Lot | SST 150FT | Van | 24hrs | Caretaker | Yes |  | PABLO ROSAL |  |  |  |  | working | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | working | OK | Ok | working | OK | OK | OK |  | WACU | WACU | Off | Condura/WCONX019ED1 | Carrier/WCARP019EA |  | F15PC-0355072 | B07PC-0023451 |  | Working | Working | Off | 8 | 9:00 |  |  |  | WORKING | Working | Off | POWERCITY | Working | Working | 25 | Working | CF100 | 4203 | Working | 201849 | Working | None |  |  | Working | N/A | Working |  | HUAWEI | Retrieved |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | ERRICSON | MINI-LINK | No |  |  |  | OK | OK | No | CATMON | HUAWEI | RTN950 | No | 8073.85 | 7763.53 | 35.9 | OK | OK | No | LUGO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  |  | 5 | 2G | [109 empty] | EMERSON | 53.7 |  | 29 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 52.4 | 52.3 | 52.2 | 52.2 | OK | 16 | TRM RACK 01 DDU 01 | 16 | TRM RACK 01 DDU 02 |  |  |  |  | 10 | RTN950 MAIN FACING LUGO |  |  | 10 | RTN950 REDUNDANT FACING LUGO | [8 empty] | 40 | BTS3012 | [35 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 17.2 | 20 | LO-EL | 50 | RECTIFIER | 20 | C.OUTLET | 50 | RECTIFIER | 30 | AIRCON 1 | 30 | AIRCON 2 | 20 | OB LIGHT | 30 | ALARM | 20 | P.LIGHT | 20 | SPARE | [20 empty] | Done | OK |  |  |  | AIRCON | 1 | CARRIER/51PMXRACCAR19KEAA07PC-0008974 | WFM | BATTERY | 2 | ACME/12NDF100 | WFM | BATTERY | 2 | NARADA/RA12-150F | WFM | MICROWAVE ANTENNA | 1 | S560674968 | TPE | MICROWAVE ANTENNA | 1 | S560674956 | TPE | MICROWAVE ANTENNA | 1 | S560205523 | TPE | MICROWAVE ANTENNA | 1 | S560207598 | TPE | [12 empty] | ELECTROMECHANICAL | GROUNDING BUSBAR | 1
V3456-Sun Cebu City Lahug 2-01102017.pdf | V3456 | SUN CEBU CITY LAHUG 2 | 2017-01-10 | Lemuel Balbuena | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | B |  |  | Residential | Rooftop | Permanent | Building | Guyed Pole 50 Ft | Van | 8am-5pm | Roving Guard | Yes | [6 empty] | n/a | N/A | N/A | N/A | Off | Building Site | Working | OK | OK | OK | OK | OK | For Rectification | OK | OK | OK | working | OK | Ok | working | OK | OK | Off |  | WACU | WACU | Off | Condura | Condura |  | T15PC-0742251 | K12PC-0416820 |  | Working | Working | Off | 8 | 8 |  |  |  |  | Working | Off |  | None | None |  | None | Off |  | None |  | None | Off |  |  | Off |  | Off | INHOUSE A1 | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI U2100/900 | Retrieved |  | Off |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Yes | 14739 | 15159 | -30 | OK | OK | Yes | V3457 GUADALUPE | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | BANAWA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | BANAWA | 1 | to rtn950 guad1 p.4 trunk | 3 | to v3456 3G u2100 | [16 empty] | GUADALUPE1 | 3 | to v3456 2G | 4 | to rtn950 banawa p.1 trunk | [47 empty] | ELTEK |  |  | 29 |  | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 |  |  | Off | [5 empty] | Off |  |  |  |  | 100 | dcdu GU900/G1800 | 100 | DCDU L850 | [30 empty] | 16 | RTN 950 FACING BANAWA | 16 | RTN950 FACING GUADA1 |  |  | EMERSON | 53.5 |  | 17 |  | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off | [5 empty] | Off | [19 empty] | 3G TURBO | 16 | RTN950 FACING 840 RDNT |  |  |  |  | 16 | RTN950 FACING GUADA1 RDNT | [31 empty] | Off | [5 empty] | Off | [86 empty] | Done | OK |  |  |  | AIRCON | 1 | CARRIER/111626958 | WFM | BATTERY | 3 BANKS | ACME | WFM | AIRCON | 1 | CARRIER/111625391 | WFM
V3459 SUN CEBU CITY MABOLO 2-02212017.pdf | V3459 | Lemuel Balbuena | 2017-02-21 |  | OK |  | N/A |  | Rectification | stolen outside grounding | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | stolen outside grounding | OK |  | OK |  | OK |  |  | Off |  |  | Commercial | Rooftop | Permanent | BUILDING | BIPOD 50 FT | Van | 8am-5pm | Roving Guard | Yes | [6 empty] | Building | N/A | N/A | OK | OK |  | Working | OK | OK | OK | OK | OK | For Rectification | OK | OK | OK | working | OK | Ok | working | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019E1 | CONDURA/WCONX019E1 |  | 51QSXRACCON19KEDB15PC-0154359 | 51QSXRACCON19KEDN13PC-0427274 |  | Working | Working | Off | 7.4 | 8.5 |  | FIREFLY |  |  | Working | Off |  | None | Working |  | None | CF100 |  | Working |  | Off | Off |  |  | Off |  | Off | BUILDING SITE | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | OK | OK | HUAWEI | 9\RTN950 | Yes |  |  | -35 | OK | OK | Yes | FACING TINAGO | HUAWEI | RTN620 | Yes |  |  |  | OK | OK | Yes | FACING TINAGO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | RTN620 FACING TINAGO | 1 | 3G | [10 empty] | RTN950 FACING TINAGO | 4 | 3G RTN950 FOR MIGRATION | [24 empty] | 1 | LTE | 3 | 2G | [68 empty] | ELTEK | 50.35 | 38 |  |  | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | No |  | 52.8 | 50.5 |  |  | Off | [16 empty] | 63 | DCDU 0 3G SMART/RTN620 |  |  | 80 | DCDU 1 |  |  | 80 | DCDU 2 |  |  | 80 | DCDU 3 | [6 empty] | 16 | RTN 950 RDNT | [6 empty] | EMERSON | 54.5 | 4 |  |  | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 |  |  |  |  | Off |  | 54.3 | 54.2 |  |  | Off | [26 empty] | 16 | RTN950 MAIN FACING TINAGO | [31 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 21.3 | 20 | LO/EL | 100 | RECTIFIER | 20 | C.OUTLET | 30 | ACU 1 | 30 | AIRCON 2 | 20 | OB LIGHT | 20 | ELTEK 2 | 30 | ALARM | 70 | ELTEK 1 | 20 | SPARE | [20 empty] | Done | OK
V3461-SUN CEBU CITY LAHUG 3-03202017.pdf | V3461 | Sun Cebu City Lahug 3 | 2017-03-20 | Lemuel Balbuena | OK |  | N/A |  | Rectification | stolen | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | stolen | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | stolen busbar | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | 4-SST 150FT | VAN | 8AM-5PM | ROVING GUARD | Yes | [6 empty] | DEFECTIVE | OK | for CSMP Endo | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | For Rehab | For Rectification | Off | OK | OK | 36557 | OK | For Rehab | N/A | OK | OK | For CSMP Endo |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CARRIER/WCARGO19EA |  | 51QSXRACCON19KED-T15PC-0722289 | 51PMXRACCAR19KEA-R12PC-0505274 |  | Working | Working | Off | 7.9 | 7.5 |  |  |  |  | None | Off |  | Off | Defective |  | Off | CF200 |  | Off |  | Off | None |  |  | Off |  | Off | INHOUSEA1 | HUAWEI | Retrieved |  | Off | HUAWEI 2100/900 | Retrieved |  | Off |  | Off |  |  | Off | None | HUAWEI/850 | Retrieved |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | NIVEL HILLS |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | NIVEL HILLS | 2 | 2G | 3 | 3G | 4 | LTE | [66 empty] | ELTEK VALERE | 54.13 | 6 |  | 60 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 52.5 | 52.3 | 52 | 51.8 | Off | [8 empty] | 80 | DCDU 850/900 | 80 | DCDU 2100 | [12 empty] | 40 | 3G MBB | [14 empty] | 16 | RTN 950 MAIN |  |  | EMERSON | 54 |  |  | 4 | 3 | 4 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | Off |  | 53 | 53 | 53 | 52.9 | Off |  |  |  |  | 3 | RTN950 RDNT | [53 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 22 | 70 | RECTIFIER | 30 | ACU 1 | 20 | C.O | 30 | ACU 2 | 20 | CABIN LIGHT | 20 | O.B. LIGHT | 20 | PERIMETER LIGHTS | 70 | ELTEK 1 | 20 | SPARE | 20 | ELTEK 2 | [20 empty] | Done | OK
v3470 SUN CEBU SAN ROQUE 2-03162017.pdf | V3470 | Sun Cebu San Roque 2 | 2017-03-16 | Lemuel Balbuena | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | Off |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | inhouse a1 | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | ROOFTOP |  | BUILDING | GUYED POLE 40 FT | VAN | 8AM-5PM | ROVING GUARD/ADMIN BLDG SECURITY | Yes | [7 empty] | Off | Off | Off | Off | BUILDING SITE | Working | OK | OK | OK | OK | OK | OK | For Rehab | OK | OK | 36617 | OK | Ok | 36526 | OK | For Rectification | Off | PORTHOLE FOR SEALANT | WACU | WACU | Off | 51QSXRACCON19KEA | 51QSXRACCON19KEA |  | B11PC-0166381 | b11pc-0166473 |  | Working | Working | Off | 8 | 10.7 |  | URA |  |  | Working | Off |  | Off | Working |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  | HUAWEI | Retrieved |  | Off | HUAWEI 2100/900 | Retrieved |  | Off |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Yes |  |  | 32.7 | OK | OK | Yes | K89 PORT AREA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | K89 PORT AREA | 1 | 2G | 2 | 3G | 3 | LTE | 4 | RTN620 P.3 CROWN REGENCY | [64 empty] | ELTEK | 53.92 |  |  | 55 | 4 | 2 | SACREDSUN | 180 | SACREDSUN | 180 |  |  |  |  | Off |  | 51.7 | 51.2 |  |  | Off | 100 | DCDU 1 | 100 | DCDU 2 | [24 empty] | 40 | DCPDB | [10 empty] | 16 | RTN950 MAIN |  |  | EMERSON | 54.4 |  |  | 2.8 | 6 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | Off |  | 54.1 | 54.1 | 54.1 | 54.1 | Off | [8 empty] | 16 | RTN950 RDNT | [49 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 30.3 | 50 | RECTIFIER | 20 | LIGHTNING | 20 | C.O | 30 | ACU 1 | 30 | ACU 2 | 20 | EMERGENCY LIGHT | 20 | SECURITY ALARM | 20 | ACU CONTROLLER | 70 | ELTEK 1 | 20 | ELTEK 2 | [20 empty] | Done | OK
V3473 SUN Mandaue Tawason.pdf | V3473 | SUN Mandaue Tawason | 2017-03-22 | Eric Brian Aligway | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK | 3-ISV3 -29.4, 5-ISV3 -32.5, 6-ISV3 -30.3 | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK | Eltek need additin 2banks battery | OK |  | OK |  | Rectification | Def. Genset | OK |  | OK |  | OK |  | OK |  | OK |  |  | B | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [43 empty] | 2 | EG4 2G (RTN950 facing V3716) | 3 | EG4 3G (RTN950 facing V3716) | 4 | EG4 LTE (RTN950 facing V3716) | [79 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3474-SUN CEBU CITY MABOLO 3-02202017.pdf | V3474 | SUN CEBU CITY ABOLO 3 | 2017-02-20 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | Off |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | POLE | OK |  | OK |  | OK |  |  | Off |  |  | Commercial | GROUND FLOOR | PERMANENT | BUILDING | POLE | VAN | 8AM-5PM | ROVING GUARD/ADMIN BLDG SECURITY | Off | [7 empty] | Off | Off | Off | Off | BUILDING SITE | Off | Off | Off | Off | Off | Off | Off | OK | OK | OK | 2000-04-01 | OK | Ok | 2000-01-01 | OK | OK | OK | REFARMING MATERIALS ONSITE | WACU | WACU | Off | CONDURAWCONX019ED1 | CARRIER/APXRT195BA |  | 51QSXRACCON19KEDT15PC-0742250 | '013914679 |  | Working | Defective | Off | 7.7 |  |  | FIREFLY |  |  | Working | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off | INHOUSE A1 | HUAWEI | Retrieved |  | Off | HUAWEI/900 | Retrieved |  | Off |  | Off |  |  | Off | Off | HUAWEI | Off |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | Z90 MABOLO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 3G | 2 | 2G | 3 | LTE | [66 empty] | HUAWEI | 54.09 | 1 |  | 36 | 4 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | No |  | 52.6 | 52.2 | 52 |  | Off | 100 | DCDU 2 | 100 | DCDU 3 | [38 empty] | 16 | RTN 950 MAIN | EMERSON | 54.6 |  |  | 15 | 6 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 54 | 54 | 54 | 54 | OK | [6 empty] | 16 | RTN950 RDNT |  |  | 10 | DC FAN | 10 | DC FAN CONTROLLER | [28 empty] | 63 | DCDU 1 | [15 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 22.9 | 20 | EMERGENCY LIGHTS | 60 | RECTIFIER 1 | 20 | CON. OUTLET | 60 | RECTIFIER 2 | 30 | ACU 1 | 30 | ACU 2 | 20 | O.B. LIGHT | 20 | SPARE | 30 | ELTEK 2 | 20 | SPARE | 70 | ELTEK 1 | 20 | SPARE | [16 empty] | Done | OK |  |  |  | AIRCON | 1 | CARRIER/13914695 | WFM
V3478 SUN MANDAUE CITY MABOLO-02222017.pdf | V3478 | SUN CEBU CITY MABOLO 1 | 2017-02-22 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | ROOFTOP | PERMANENT | BUILDING | GUYED POLE 30FT | VAN | 8AM-5PM | ROVING GUARD | Yes | [7 empty] | Off | Off | Off | Off | BUILDING SITE | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 0/4 SWITCH FOR CHECKING | OK | Ok | URA/BBT-10C | OK | OK | Off |  | WACU | WACU | Off | CONDURAWCONX019ED1 | FP-51PMXRACCARP19FEDP3C |  | 51QSXRACCON19KEDN14PC-0568122 | 51PMXRACCAR19KEDN07PC-0376852 |  | Working | Defective | Off | 9.1 |  |  | URA/BBT-10C |  |  | Working | Off |  | None | None |  | None | CF200 |  | Working |  | Off | Off |  |  | Off |  | Off | BUILDING SITE | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Off |  |  | 32 | OK | OK | Yes | FACING NAWANAO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 2 | 3G | 3 | 2G | 4 | LTE | [66 empty] | ELTEK | 53.79 |  |  | 42 | 4 | 3 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 |  |  | Off |  | 52.5 | 52.4 | 52.2 |  | OK | 100 | DCDU 1 | 100 | DCDU 2 | 100 | DCDU 3 | [36 empty] | 16 | RTN950 MAIN FACING NAWANAO | EMERSON | 53.9 |  |  | 5 |  |  | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.7 | 53.7 | 53.7 |  | Off | [24 empty] | 16 | RTN950 RDNT FACING NAWANAO | [33 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 22 | 20 | LIGHTNING | 100 | RECTIFIER | 20 | C.O | 30 | ACU 2 | 30 | ACU 2 | 20 | O.B LGHT | 20 | SPARE | 20 | ALARM |  |  | 20 | SPARE | 70 | ELTEK 2 | 70 | ELTEK 1 | [16 empty] | Done | OK
V3479_SUN Mandaue-Looc_PMR.pdf | V3479 | MANDAUE_CENTRO / (v3479) SUN - Mandaue City-Looc | 2017-02-16 | Jerome T. Butong | OK | On going refarming activity | N/A |  | Rectification | for busbar installation (indoor and outdoor) | N/A |  | Rectification | no busbar | OK |  | Rectification | no busbar | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | no mains, all batteries has been stolen | Rectification | no busbar | OK |  | N/A |  | N/A |  | N/A |  | Rectification | no busbar | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | N/A | no battery(battery has been stolen on site) | N/A | no battery(battery has been stolen on site) | N/A |  | N/A | building site | N/A | building site | OK |  | Rectification |  | Rectification | ACU's for checking | Rectification | excess materials for pull out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3480 SUN Compostela.pdf | V3480 | SUN Compostela | 2017-02-06 | G.Vale/ A. Ambil | OK | VSWR all are 1.1. | N/A | Not applicable. | Rectification | Stolen outdoor grounding. | N/A | Not applicable. | N/A |  | OK | ok. | OK | ok. | OK | ok. | OK |  | N/A | Not applicable. | OK | ok. | Off |  | Off |  | Off |  | OK | OK. | OK | OK | OK |  | OK | OK. | OK | OK. | N/A | NOT APPLICABLE. | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK | OK. | OK | 3 hours for Eltek. | OK | ok green light. | OK |  | N/A | NOT APPLICABLE. | OK | ok. | OK | Stolen bus bard, stolen outdoor grounding. | OK |  | OK |  | OK |  |  | Off |  | Brgy Poblacion, Compostela, Cebu | Residential | Lot | Permanent | Lot | SST 60m | Van | 24 hours | Caretaker | Yes |  | UNKNOWN | NA | 10.451 | 124.0102 | UNKNOWN | 0, 4 | For Repair | OK | for Replacement | OK | PADLOCK FOR REPLACEMENT | Defective | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | 4, 0 | OK | Ok | 1, 0 | OK | OK | For CSMP Endo | for cleaning. | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 | NONE | 51QSXRACCONX19KED T15PC-0742040 | 51QSXRACCONX19KED M14PC-0516779 | NONE | Working | Working | Off | 8.0 A | 8.0 A | NA | ERICSSON TELECOOL FC-S | NONE | NONE | Working | Off | NONE | None | Working | NONE | Working | CF200 | NONE | Working | 96201-C | None | None | NOT APPLICABLE | 01 000 816 | Off | NOT APPLICABLE | None | NO GENSET, ATS AND TANK | BTS3900 | Retrieved | NONE | Off | BTS3900 | Off | NONE | Off | NONE | Off | NONE |  | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | ERICSSON | Minilink-E | No | to follow not accesible | to follow not accesible | -36dBm | OK | OK | No | 805 Danao (for decom) | Huawei | RTN950 | Yes | 8118.32/8059.02/8088.67 | 7807/7747.7/7777.35 | -36dBm | OK | OK | Yes | 805 Danao | Huawei | RTN950 | Yes | to follow not accesible | to follow not accessible |  | Off | OK | Yes | V3604 Mitsumi(not used) | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off |  | Off |  | none |  |  |  | none |  |  |  | none |  |  |  | none |  | Off | Off | Off | none |  | Off | Off | Off | none |  | Off | Off | Off |  | Ericsson Minilink-E facing V3604 | 1 | V3480 SUN Compostela 2G (for e1 migration) | [10 empty] | none | [12 empty] | none | [12 empty] | EG4 RTN950 facing 805 Danao | 1 | VACANT | 2 | VACANT | 3 | V3480 SUN COMPOSTELA 3G (To UMPT) | 4 | VACANT | [12 empty] | EG4 RTN950 facing V3604 | 1 | VACANT | 2 | VACANT | 3 | VACANT | 4 | VACANT | [13 empty] | none | [29 empty] | ELTEK | 53.82 | 0 | 32 | 32 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE |  | No |  | 53.7 | 53.9 | 53.9 | 53.7 | Off | 100 | DCDU 12B L700/L1800 | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | DCDU 12B TURBO G900 | 63 | HUAWEI 3900 | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | SPARE | 20 | RTN950 FACING V3604 SABANG MAIN | 20 | RTN950 FACING 805 DANAO MAIN | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | EMERSON | 53.4 | 0 | 19 | 19 | 4 | 1 | SACRED SUN | 180 | NONE |  | NONE |  | NONE |  | No |  | 53.3 |  |  |  | Off | 16 | TRM CABINET 01 PLATE A1 | 16 | TRM CABINET 01 PLATE A2 | 16 | RTN950 REDUNDANT FACING 805 DANAO | 16 | SPARE | 10 | RTN950 REDUNDANT FACING V3604 SABANG | 10 | HEAT EXTRACTOR | 10 | HEAT EXTRACTOR | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 50 | SPARE | 50 | SPARE | 50 | SPARE | 40 | SPARE | 25 | SPARE | 25 | SPARE | 25 | SPARE | 25 | SPARE | [6 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 20 | LIGHTINGS EMERGENCY LIGHT | 60 | EMERSON 1 X2 | 20 | CONVENIENCE OUTLET | 60 | EMERSON 2 X4 | 30 | ACU1 | 30 | ACU2 | 20 | OB LIGHT | 20 | PERIMETER LIGHT | 30 | ELTEK2 | 20 | SPARE | 70 | ELTEK1 | 20 | SPARE | [16 empty] | Done | OK | [134 empty] | Gate for repair
V3481 SUN Consolacion Jugan.pdf | V3481 | SUN Consolacion Jugan | 2017-02-21 | G. Vale | OK | All are 1.1 to 1.2. | OK |  | Rectification | stolen grounding cables and busbar. | N/A |  | N/A |  | Off |  | OK |  | OK | New RTN950 facing SUN Liloan Poblacion not yet accepted with alarms possible no far end yet. | OK | New RTN950 facing SUN Liloan Poblacion not yet accepted with alarms possible no far end yet. | N/A |  | OK |  | OK | DONE FOR 3G. NO LTE YET. | Off | All MW are -34dBm. | OK |  | OK |  | Rectification | ok. | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | ok, please data below for rectifiers. | OK | 4 hours back-up. | OK |  | OK |  | OK |  | OK |  | OK | STOLEN OUTDOR BUS BAR | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 2017-02-21 | BRGY PITOGO, CONSOLACION, CEBU | COMMERCIAL | LOT | PERMANENT | LOT | 4 LEGGED SST 50METERS | VAN | 24 HOURS | CARETAKER | Yes | 2017 | QUIAPO family | UNKNOWN | 123.9724 | 10.3824 | PITOGO, CONSOLACION | 5, 0 | OK | OK | OK | OK |  | Working | OK | OK | OK | Off | For Rehab | For Rectification | For Rehab | OK | OK | 4, 0 | OK | Ok | NONE | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | WCONX019ED1 | NONE | 51QSXRACCON19KED T15PC-0715765 | 51QSXRACCON19KED C15PC-0263878 | NONE | Working | Working | None | 7.8 | 7.8 | NONE | ERICSSON/TELECOOL FC-S | NONE | 1, 0 | Working | None | WEICHAI | Working | Working | 20 | Working | CF200 | 403 | Working | VECO 0999 EGS0 | Working | None | 200 L | 13674491 | Working | 0 | Working | WEICHAI SN: 070511252F | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | NONE | Off | NONE | NONE | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | HUAWEI | RTN950 | Yes | UNABLE TO ACCESS |  | -34 | OK | OK | Yes | FACING PAKNAAN | HUAWEI | RTN950 | Yes | 7866.30/7895.95 | 8177.5/8207.27 | -34 | OK | OK | Yes | FACING JAGOBIAO | HUAWEI | RTN620 | Yes | 1507 | 14627 | -34 | OK | OK | Yes | FACING MDE003 PAKNAAN | HUAWEI | RTN620 | Yes | 15307 | 14887 | -34 | OK | OK | Yes | FACING V3497 SUN LILOAN POB | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  | RTN620 FACING MDE003 | 11 | V3497 SUN LILOAN POB 2G 1XE1 | [10 empty] | RTN620 FACING V3497 SUN LILOAN | 3 | V3497 SUN LILOAN POB 2G 1XE1 | [23 empty] | EG4 RTN950 FACING V5139 PAKNAAN | S1-P1 | VACANT | S1-P2 | AGG. FOR V3491 JAGOBIAO 2G/3G (TO RTN950 S1-P2) | S1-P3 | V3481 JUGAN 3G (TO UMPTb1) | S1-P4 | V3497 LILOAN POB 3G | [12 empty] | EG4 RTN950 FACING JAGOBIAO | S1-P1 | VACANT | S1-P2 | AGG. FOR V3491 2G/3G (FROM S1-P2 FACING V5139) | S1-P3 | VACANT | S1-P4 | V3481 CONSOLACION JUGAN 2G PABIS (TO gtmu) | [5 empty] | EMS6 RTN620 FACING V3497 SUN LILOAN | S8-P2 | V3497 SUN LILOAN POB 3G (from s1-p4 facing V5139) |  |  |  |  | NONE |  |  | NONE | [27 empty] | ELTEK | 54.19 | 0 | 4 | 4 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.9 | 53.9 | 53.9 | 53.9 | OK | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | RTN950 FACING V5139 PAKNAAN | 16 | RTN950 FACING V3491 JAGOBIAO | 16 | SPARE | 16 | SPARE | ELTEK | 54.33 | 3 | 73 | 73 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.7 | 53.7 | 53.7 | 53.7 | OK | 100 | DCDU U900/L850 | 100 | DCDU L700/L1800 | 100 | SPARE | 100 | DCDU G1800 | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | ALL RTN620 | 63 | SPARE | 40 | DCDU U2100 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 16 | SPARE | 16 | SPARE | 16 | FMS | 16 | RTN950 MAIN FACING V3497 LILOAN | 16 | RTN950 RED FACING V3497 LILOAN | 16 | RTN950 MAIN FACING V5139 PAKNAAN | 16 | RTN950 MAIN FACING V3491 JAGOBIAO | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 20 | LIGHTINGS/EMERGENCY LIGHT | 60 | ELTEK1 | 20 | CONVENIENCE OUTLET | 60 | ELTEK2 | 30 | ACU1 | 30 | ACU2 | 20 | OB LIGHT | 20 | PERIMETER LIGHT | 30 | ELTEK L2 | 20 | SPARE | 70 | ELTEK L1 | 20 | SPARE | [16 empty] | Done | OK | ELTEK1 SN:163124001257 ELTEK2 SN:150224000710 | PERCIVAL QUIJANO | 2/2/1/2017 | SUPPORT | 1 | Carrier APXRM195BA SN: 013532065 | WFM | SUPPORT | 1 | Carrier APXRM195BA SN: 013537431 | WFM | SUPPORT | 1 | EMERSON ACTURA SN: A084005117 | WFM | [28 empty] | SUPPORT | GROUNDING | 1 | NONE | NONE | NONE | N/A | SUPPORT | VAN FLOORING | 1 | NONE | NONE | NONE | FOR REHAB
V3482SUN_CORDOVA_GABI.pdf | V3482 | SUN-Cordova-Gabi | 2017-03-01 | Astrobal A. Trozo | OK |  | N/A | no combiners | N/A | STOLEN BUSBAR | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A | no access point | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A | stolen busbar | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK | excess refarming materials for pull out c/o huawei | OK |  | PERCIVAL B. QUIJANO | B | 42795 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3486 Danao Guinsay.pdf | V3486 | Danao Guinsay | 2017-02-22 | G. Vale | OK |  | N/A |  | Rectification | stolen grounding | N/A |  | N/A |  | OK |  | OK |  | OK | OK. | OK |  | N/A |  | OK |  | OK | DONE FOR 3G ONLY. | Off | -35dBm for both MLTN and RTN950. | OK |  | OK |  | OK | outdoor grounding stolen. | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | ok all. | OK | 4 hours back-up. | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 2017-02-22 | BRGY. DUNGGUAN, DANAO CITY, CEBU | COMMERCIAL | LOT | PERMANENT | LOT | GUYED 32M | VAN | 24 HOURS | CARETAKER | Yes | 2017 | DURANO LOT | UNKNOWN | 124.0224 | 10.5523 | UNKNOWN | 3, 1 | N/A | OK | OK | OK |  | Working | OK | OK | OK | OK | For Rehab | OK | OK | OK | OK | 2, 0 | OK | Ok | NONE | OK | OK | OK |  | WACU | WACU | Off | WCONH019ED | WCARG019EA | NONE | 51QSXRACCON19KEDJ16PC-0975052 | 51PMXRACCAR19KEAH13PC-0289069 |  | Working | Working | None | 7.8 | 7.1 | NONE | NONE | NONE | NONE | None | None | N/A | None | Defective | N/A | None | CF200 | N/A | Working | 245731 | None | None | N/A | 207NM023571 | Off | NONE | None |  | BTS3900A | Retrieved | NONE | Off | BTS3900 | Off | NONE | Off | NONE | Off | NONE |  | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | HUAWEI | RTN950 | No | to follow | to follow | -36dBm | OK | OK | Yes |  | ERICSSON | MLTN | No | TO FOLLOW | TO FOLLOW | -36dBm | OK | OK | No |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off | Off | Off |  | none |  | Off |  |  |  | Off |  | Off |  | none |  |  |  | none |  |  |  | none |  |  |  | none |  | Off | Off | Off | none |  | Off | Off | Off | none |  | Off | Off | Off |  | ERICSSON MLTN | 1 | V3486 DANAO GUINSAY 2G 1XE1 | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | EG4 RTN950 FACING SUBA | S6-P1 | VACANT | S6-P2 | VACANT | S6-P3 | V3486 DANAO GUINSAY 3G | S6-P4 | VACANT | [14 empty] | NONE | [19 empty] | NONE | [29 empty] | EMERSON | 54.4 | 0 | 29 | 29 | 3 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | No |  | 53.2 | 53.1 | 53.1 | NONE | Off | 6 | SPARE | 6 | RTN950 FACING SUBA MAIN | 16 | TRM1 ERICSSON MLTN | 16 | RTN950 REDUNDANT FACING SUBA | 40 | WCDMA | 50 | SPARE | 50 | DCDU 3G 2100 | 50 | SPARE | 50 | SPARE | 50 | SPARE | 50 | SPARE | 6 | SPARE | [20 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 125 |  | 70 | RECTIFIER | 30 | ACU1 | 20 | LIGHTING | 30 | ACU2 | 15 | CO | 15 | OB LIGHT | 15 | PERIMETER LIGHT | 20 | SPARE | 15 | SPARE | 20 | SPARE | [20 empty] | Done | OK | EMERSON SN: 21010705842081EA005B | PERCIVAL QUIJANO | 2017-02-22 | BTS3012 | 2 | UNREADABLE | BUILD | [36 empty] | SUPPORT | GROUNDING | 1 | [88 empty] | Stolen grounding and need grass-cutting.
V3487 Danao Taytay.pdf | V3487 | Danao Taytay | 2017-02-22 | G. Vale | OK | All ok 1.1 to 1.4. | N/A |  | Rectification |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | 3G is blocked due to TX 1xE1 only. | Off | Minilink TN: -33dBm. RTN950 on going installation | OK |  | OK |  | Rectification |  | OK |  | OK |  | N/A |  | N/A |  | N/A | no 19 inch rack sine outdoor. | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK | 1 bank 150Ah only, newly installed c/o Fulrubel. Old battery pulled-out by Fulrubel. | OK |  | OK |  | N/A | No genset and ATS. | OK |  | OK | BUSBAR STOLEN | N/A | Outdoor site | Rectification | Need grasscutting. | OK |  | PERCIVAL QUIJANO | A | 2017-02-22 | BRGY. TAYTAY, DANAO, CEBU | RESIDENTIAL | LOT | PERMANENT | LOT | GUYED 32M | NONE | 24 HOURS | N/A | Yes | 2017 | UNKNOWN | UNKNOWN | 124.0251 | 10.5324 | UNKNOWN | 0, 4 | N/A | OK | OK | For CSMP Endo | NEED GRASSCUTTING | Working | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | N/A | OK | Ok | NONE | OK | OK | Off | OUTDOOR SITE | Off | Off | Off | NONE | NONE | NONE |  |  |  | None | None | None |  |  |  | NONE | NONE | NONE | Off | Off | N/A | None | Off | N/A | None | Off | N/A | Working | 270247 | None | None | N/A | 209NM085303 | Off | N/A | None |  | BTS3012 | Retrieved | NONE | Off | BTS3900 | Off | NONE | Off | NONE | Off | NONE |  | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | ERICSSON | MLTN | No | 15874 | 15943 |  | OK | OK | No | FACING V3530 SUBA |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off |  | NONE | [11 empty] | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  |  | Off | Off | Off |  | MINILINK TN | 1 | V3487 Danao Taytay 2G 1xE1 | 2 | V3487 DANAO TAYTAY 3G 2XE1 blocked | 3 | V3487 DANAO TAYTAY 3G 2XE1 blocked | [33 empty] | NONE | NONE | [20 empty] | NONE | [19 empty] | NONE | [29 empty] | HUAWEI BTS3012 | N/A | N/A | N/A | N/A | 3 | 1 | SACRED SUN | 150 | NONE | NONE | NONE | NONE | NONE | NONE | Off |  | 53.9 | NONE | NONE | NONE | Off | 40 | WCDMA 3G | 16 | MINILINK TN | 16 | RTN950 MAIN ON-GOING INSTALLATION | 16 | RTN950 RED ON-GOING INSTALLATION | [36 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | none | [14 empty] | Off | [5 empty] | Off | [44 empty] | 100 |  | 50 | BTS3012 | 20 | SPARE | 20 | PERIMTER LIGHTS | 20 | SPARE | 20 | SPARE | 20 | SPARE | [28 empty] | Done | OK |  | PERCIVAL QUIJANO | 2017-02-22 | [40 empty] | SUPPORT | PERIMETER LIGHT | [5 empty] | SUPPORT | RECT. BATTERY |  | LOW BACK |  |  | 1 BANK ONLY | [74 empty] | Need new rectifier outdoor cabinet to accommodate more batteries and back-up power.
V3488 Danao Looc.pdf | V3488 | SUN Danao City Looc | 2017-02-27 | G. Vale | OK | VSWR ok 1.1. | N/A |  | Rectification |  | Off |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | done for 3G, Tx is 2xE1. | OK | -36dBm. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | no Bro. | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK | ok. | OK |  | OK |  | OK |  | N/A | SITE NO GENSET. | OK |  | OK |  | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 42793 | BRGY TUBURAN, DANAO CITY, CEBU | RESIDENTIAL | LOT | PERMANENT | LOT | GUYED 32M | VAN | 24 HOURS | N/A | Yes | 2018 | UNKNOWN | UNKNOWN | 124.0112 | 10.5116 | UNKNOWN | 0, 4 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | 2, 0 | OK | Ok | NONE | OK | OK | OK |  | WACU | WACU | Off | WCONX019ED1 | FP-51PMXRACCARP19KEDP3C | NONE | 51QSXRACCON19KED T15PC-0756883 | 51PMXRACCAR19KEDT09PC-0537739 |  | Working | Working | None | 7.9 | 6.9 | N/A | none | none | N/A | None | None | N/A | None | Working | N/A | None | CF200 | N/A | Working | 270244 | None | None | none | 209NM085307 | Off | none | None | SITE NO GENSET AND ATS | BTS3900 | Retrieved | NONE | Off | BTS3900 | Off | NONE | Off | NONE | Off | NONE |  | Off | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | HUAWEI | RTN950 | Yes | to follow | to follow | to follow | OK | OK | Yes | FACING 805 DANAO | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  | RTN950 FACING 805 DANAO | 42737 | V3488 Danao Looc 2G 2xE1 | 42798 | V3488 Danao Looc 3G 2xE1 | [10 empty] | NONE | [12 empty] | NONE | [12 empty] | NONE | [20 empty] | NONE | [19 empty] | NONE | [29 empty] | EMERSON | 54.5 | 0 | 24 | 24 | 5 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN | 150 | NONE | SACRED SUN | No |  | 53.8 | 53.8 | 53.8 | NONE | Off | 6 | SPARE | 6 | RTN950 FACING 805 DANAO RED | 16 | SPARE | 16 | RTN950 FACING 805 DANAO MAIN | 40 | 2G | 40 | WCDMA | 50 | SPARE | 50 | SPARE | 50 | SPARE | 50 | SPARE | 50 | SPARE | 50 | SPARE | 50 | BAU | [18 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 125 | 70 | RECTIFIER | 32 | ACU1 | 20 | C-LIGHT | 32 | ACU2 | 20 | C-OUTLET | 20 | OB LIGHT | 20 | ALARM | 20 | SPARE | 20 | PERIMETER LIGHT | 20 | SPARE | [20 empty] | Done | OK | EMERSON SN: 210107058421044A0058 | PERCIVAL QUIJANO | 42793 | [40 empty] | SUPPORT | PERIMETER LIGHT |  |  |  |  | N/A
V3492 Sun-LLC-Marigondon 2.pdf | V3492 | SUN - Lapu-Lapu City-Marigondon 2 | 2017-02-20 | Astrobal A. Trozo | OK |  | N/A |  | Rectification | no busbar, stolen | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | waiting for IT for the huawei software installation | N/A | waiting for IT for the huawei software installation | Rectification | for huawei rectification | OK |  | N/A | no busbar, stolen | OK |  | OK |  | N/A |  | N/A |  | N/A | outdoor site | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A | building site | OK |  | OK |  | N/A | outdoor site | Rectification | excess materials for pull out; 2 banks battery for arda(North Star); panel antennas for arda | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3494 Sun Agus Checklist.pdf | V3494 | Sun Lapu-lapu City Agus | 2017-03-01 | Eddie D. Clave Jr. | OK | for 3g all vswr passed <1.2 | OK |  | Rectification | Stolen tower grounding busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For re-labeling | Rectification | For cabling of external alarms via Emerson(refarm); Missing controller for Eltek | Rectification | stolen tower grounding busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | missing eltek controller(smartpack); for replacement of emerson rectifier; for replacement of 4 banks 100AH Narada | Off |  | Rectification | TVSS OB light no light for checking | OK |  | Rectification | genset fuel leak when operating for CSMP checking | OK |  | Rectification | stolen grounding busbar on tower | Rectification | for roofing rehab; excess mats on site for pull-out; porthole for sealanat | Rectification | for grass uprooting and clean-up | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3495Dapitan.pdf | V3495 | SUN CORDOBA DAPITAN | 2017-01-16 | Astrobal A. Trozo | OK |  | N/A |  | Rectification | stolen | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | waiting for IT for the installation of Huawei Software | N/A | waiting for IT for the installation of Huawei Software | OK |  | OK |  | N/A | stolen busbar | OK |  | OK |  | N/A | stolen busbar | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | no genset | OK |  | OK |  | OK |  | Rectification | major grass cutting and excess materials for pull out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3497 SUN Liloan Pob.pdf | V3497 | SUN Liloan Poblacion | 2017-01-20 | G. Vale | OK |  | N/A |  | Rectification |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A | ROOFTOP UNDER LILOAN MUNICIPAL HALL | OK |  | PERCIVAL QUIJANO | A | 42755 | Rooftop of Liloan Municipal Hall, Liloan, Cebu | Government | Rooftop | PERMANENT | Building | Bipod | VAN | 8am-5pm | N/A | Yes |  | Liloan Municipality | UNKNOWN |  |  | Liloan, Cebu | 0, 1 | N/A | N/A | OK | For CSMP Endo | ROOFTOP SITE, AREA UNDER MUNICIPAL HALL OFFICES | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 1, | OK | Ok | 0, 1 | OK | OK | OK |  | WACU | WACU | Off | WCONH019ED | FP-51MXRACCAR19KEDP3C | NONE | 51QSXRACCON19KEDK16PC-1074599 | 51PMXRACCAR19KEDT09PC-0529988 | NONE | Working | Defective | None | 7 | DEFECTIVE-0 |  | NONE | NONE | NONE | None | None | NONE | None | Working | NONE | None | Off | NONE | None | NONE | None | None | NONE | NONE | Off | NONE | Defective |  | BTS3900 | Retrieved | NONE | Off | BTS3900 | Retrieved | NONE | Off | NONE | Off | NONE | NONE | Off | Off | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | HUAWEI | RTN620 | No | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | No | FACING V3481 CONSOLACION JUGAN | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  | RTN620 | 3 | V3497 SUN LILOAN 2G 1XE1 | [12 empty] | NONE | [12 empty] | NONE | [10 empty] | EMS6 RTN620 | S6-P1 | V3497 SUN LILOAN 3G | [20 empty] | NONE | [19 empty] | NONE | [29 empty] | ELTEK | 53.8 | 0 | 43 | 43 | 4 | 3 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | SACRED SUN | No |  | 53.5 | 53.6 | 53.5 | NONE | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | BTS3012 2G | 40 | 3G | 40 | RTN620 POWER | 40 | DCDU U2100 | 40 | SPARE | 40 | SPARE | 40 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | 16 | SPARE | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 100 |  | 70 | ELTEK1 | 70 | ELTEK1 | 30 | ACU1 | 30 | ACU2 | 20 | C.O | 20 | SPARE | 20 | LIGHTINGS | 20 | SPARE | [24 empty] | Done | OK | ELTEK SN: 155224000426 | PERCIVAL QUIJANO | 42788 | CARRIER |  | MODEL: WCARP019EA SN: 11602531 | [37 empty] | SUPPORT | ACU2 |  | CARRIER |  |  | DEFECTIVE PLS SEE ABOVE
V3499Sun-LLC-Marigondon 3.pdf | V3499 | SUN-Lapu-Lapu City-Marigondon 3 | 2017-02-16 | Astrobal A. Trozo | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A | waiting for IT for Huawei software installation | N/A | waiting for IT for Huawei software installation | N/A | under huawei rectification (refarming activity) | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | excess materials for pull out; for grass cutting | OK |  | PERCIVAL B. QUIJANO | B | 2017-02-16 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3500SUN - LAPU-LAPU CITY-LOOC.pdf | V3500 | LPU_LOOC / (V3500) SUN - LAPU-LAPU CITY-LOOC | 2017-02-07 | Astrobal A. Trozo | OK |  | N/A |  | N/A | stolen busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A | waiting for IT for the huawei software installation | N/A | waiting for IT for the huawei software installation | OK |  | OK |  | N/A | stolen busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Off |  | N/A | no genset | OK |  | OK |  | OK |  | Rectification | excess materials for pull out; | OK |  | PERCIVAL B. QUIJANO | B | 2017-02-07 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3505 SUN MANDAUE SUBANGDAKU 1-02212017.pdf | v3505 | SUN MANDAUE CITY SUBANGDAKU 1 | 2017-02-21 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | FOR RECTIFICATION BY CONTACTOR | Rectification | FOR CLEANING | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | ROOFTOP |  | BUILDING |  |  | 8AM-5PM |  | Off | [7 empty] | Off | Off | Off | Off | BUILDING SITE | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2000-02-01 | OK | Ok | N/A | OK | OK | For CSMP Endo |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CONDURA/WCONX019ED1 |  | 51QSXRACCON19KEDT15PC-0756816 | 51QSXRACCON19KEDN14PC-0558066 |  | Working | Working | Off | 8.1 | 8.3 |  |  |  |  | None | Off |  | None | None |  | None | CF200 |  | None |  | None | Off |  |  | Off |  | None |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI 900 | Retrieved |  | Off |  |  | Off | Off | HUAWEI 2100/850/700 | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Yes |  |  | 35 | OK | OK | Yes |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | RTN950 FACING MABOLO | 1 | 2G | 2 | 3G | 3 | LTE | [66 empty] | ELTEK | 53.85 |  |  | 71 | 4 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 50.2 | 49.9 | 49.8 | 49.7 | OK | 100 | DCDU 1 | 100 | DCDU 2 | 100 | DCDU 3 | [36 empty] | 16 | RTN950 MAIN | EMERSON |  |  |  | 3 | 4 | 4 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 | No |  | 53.3 | 53.2 | 53.1 | 53 | OK | [12 empty] | 16 | RTN 950 RDNT | [45 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 28 | 70 | RECTIFIER | 30 | ACU 1 | 20 | LIGHTNING | 30 | ACU 2 | 15 | C.O | 15 | O.B LIGHT | 70 | ELTEK 1 | 20 | SPARE | 15 | SPARE | 20 | ELTEK 2 | [20 empty] | Done | OK |  |  |  | BATTERY | 3 BANKS | SACRED SUN FTB12-100 | WFM
V3512 Sun Pajac1 Checklist.pdf | V3512 | Sun Lapu-lapu City Pajac1 | 2017-03-02 | Eddie D. Clave Jr. | OK |  | OK |  | Rectification | stolen grounding busbar(indoor & outdoor) | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For re-labelling | Rectification | for external alarm cabling (refarm) | Rectification | stolen busbars | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | Off |  | N/A |  | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | for sweeping | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3513 Sun Maribago.pdf | V3513 | Sun Lapu-lapu City Maribago | 2017-03-16 | Eddie D. Clave Jr | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A | rru on top | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | for ext alarm recabling | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | Rectification | defective genset | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | for site grasscutting | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3514-SUN SAN REMEGIO POBLACION-03302017.pdf | V3514 | SUN SAN REMEGIO POBLACION | 2017-03-30 | JEROME BUTONG | OK |  | N/A |  | Rectification | STOLEN OUTSIDE GROUNDING | N/A |  | N/A |  | Off |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | STOLEN INSIDE GROUNDING | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | DEFECTIVE BATTERY/NO ATS | OK |  | OK | STOLEN GROUNDING | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | 4-SST 150FT | VAN | 24HRS | CARETAKER | Yes | [6 empty] | DEFECTIVE/TRIPPED BREAKER | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | For Rehab | For Rectification | OK | OK | OK | 36617 | OK | Ok | WORKING | OK | OK | Off |  | WACU | WACU | Off | CARRIER/APXRM195BA | CONDURAWCONX019ED1 |  | 13537454 | 51QSXRACCON19KEDR14PC-0592294 |  | Working | Off | Off | 9 | 7.8 |  | URA/BBT-10C |  | DEFECTIVE BATTERY | Working | Off | SDG25 | None | None | 25 | Working | CF200 | DEFECTIVE | Working |  | None | None | 90 LITERS |  | For CSMP Endo | N/A | None |  | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | OK | OK | ERRICSON | MINI-LINK | Yes |  |  |  | OK | OK | Yes | BOGO | HUAWEI | RTN950 | No |  |  |  | OK | OK | Yes | FACING V3449 SUN BOGO | HUAWEI | RTN950 | No |  |  |  | Off | Off | Off | FACING 813 BOGO |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | FACING CAPUTATAN SUR | 1 | 1ST E1 2G | 2 | 2ND E1 2G | [107 empty] | EMERSON | 54.2 |  |  | 34A | 4 | 2 | SACREDSUN | 100 | SACREDSUN | 100 |  |  |  |  | Off | [5 empty] | Off | 16 | TMR9202 DCPDB A1 | 16 | TMR9202 DCPDB A2 | 16 | RTN950 BOGO MAIN | 16 | RTN950 BOGO REDUNDANT |  |  | 10 | HEAT EXTRACTOR | 10 | HEAT EXTRACTOR | [10 empty] | 50 | BTS3900L UPPER | 50 | BTS3900L LOWER | [6 empty] | 16 | RTN 950 FACING SMART BOGO MAIN | 16 | RTN 950 FACING SMART BOGO REDUNDANT | [21 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 25.49 | 20 | EMERGENCY LIGHTS | 60 | RECTIFIER X2 MODULES | 20 | CONVENIENCE OUTLET | 60 | RECTIFIER X4 MODULES | 30 | ACU 1 | 30 | ACU 2 | 20 | OBSTRUCTION LIGHT | 20 | PERIMETER LIGHTS | 30 | SPARE | 20 | SPARE | 20 | SPARE | 20 | SPARE | [16 empty] | Done | OK | OUTDOOR RECTIFIER AND EQUIPMENT NOT USED/ 3 BANKS SACREDSUN 180AH/ 1 BATTERY CABINET NOT USED/17Q1-1925
V3530 Danao Suba.pdf | V3530 | Danao City Suba | 2017-02-23 | G. Vale | OK |  | N/A |  | Rectification | Stolen grounding cables and busbar. | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK | Done for 3G and LTE TDD. | OK | All are -35 dBm to -38dBm.. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | Rectification | ELTEK defective battery 2banks Acme Narada 155Ah. About 15 minutes back-up only. | OK |  | OK |  | OK | WITH GENSET but NO ATS. | OK |  | OK |  | OK |  | Rectification | Photocell not working properly. | OK |  | PERCIVAL QUIJANO | A | 42788 | BRGY SUBA, DANAO CITY | COMMERCIAL | LOT | PERMANENT | LOT | 32 m | VAN | 24 H | CARETAKER | Yes |  | UNKNOWN | UNKNOWN | 124.0251 | 10.5212 | UNKNOWN | 2, 1 | OK | OK | OK | For CSMP Endo |  | Defective | OK | OK | For Rehab | OK | OK | For Rectification | OK | OK | OK | 2, 0 | OK | For Rehab | NONE | OK | OK | OK |  | WACU | Off | Off | FP-51PMXRACCARP19KEDP3C | FP-51PMXRACCARP19KEDP3C | NONE | 51PMXRACCAR19KEDT07FC-0479252 | 51PMXRACCAR19KEDT07FC-0433428 | NONE | Working | Defective | None | 7 | NONE | NONE | NONE | NONE | 1, 0 | None | None | POWERCITY | None | Working | 25 | Working | CF200 | 110 | Working | 316328 | Working | None | 150L | 2BMNM355390 | Working | 1 | Working | POWERCITY GENSET SN: G14070862 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Retrieved | DECOM | Off | BOSER | 6 | Retrieved | Off | NONE | Off | BTS3900 | Retrieved | NONE | Off |  | OK | OK | AVIAT | HARRIS ECLIPSE | No | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | Yes | FACING 805 DANAO | HUAWEI | RTN950 | No | TO FOLLOW | TO FOLLOW | TO FOLLOW | OK | OK | Yes | FACING V3486 GUINSAY | HUAWEI | RTN950 | No | 14151 | 14935 | -33dBm | OK | OK | Yes | FACING V3487 TAYTAY | HUAWEI | RTN980 | Yes | 8177.62 | 7800.3 | -34dBm | OK | OK | Yes | FACING 805 DANAO | ERICSSON | MLTN | No | 14980 | 14141 | -37dBm | OK | OK | No | FACING V3487 DANAO TAYTAY | NONE |  | Off |  |  |  | Off |  | Off | NONE | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | ECI | APOLLO | Yes | Trad | Yes | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  | AVIAT HSTX DAC16 SLOT3 | 42738 | V3530 DANAO SUBA 2G 3XE1 | 42830 | V3486 GUINSAY 2G 2XE1 | 6 | V3487 Danao Taytay 2G 1x1 | 16 | RTN NMS | 43051 | V3487 DANAO TAYTAY 3G BLOCKED 2XE1 |  |  | ERICSSON MINILINK | 1 | V3486 GUINSAY 2G | 2 | V3487 TAYTAY 2G | 42798 | V3487 TAYTAY 2XE1 3G | [8 empty] | NONE | [10 empty] | AVIAT FACING 805 DANAO | S9-P1 | TO RAC6XE | S9-P2 | V3530 DANAO SUBA LTE TDD | S9-P3 | DEFECTIVE | S9-P4 SFP | UPLINK VIA ECI FS 1GE (to u0/0) | S9-P5 SFP | CONNECTED TO SLOT10-P5 | S10-P1 | V3530 WIMAX DECOM | S10-P2 | V3530 SUBA BRO TO BOSER ROUTER | S10-P3 | V3530 SUBA 3G (TO UMPTb) | S10-P4 SFP | V3486 DANAO GUINSAY 3G (TO RTN950 S6-P3) | S10-P5 SFP | CONNECTED TO SLOT9-P5 | ALLIED SWITCH TURBO | 2 | RTN NMS | 4 | AGGREGATE PORT (TO RTN980 S4-P3)/V3480 L700 | 20 | TRUNK TO PMANDAUE (TO ECI FS u0/1) | [14 empty] | 42737 | FACING F70LILOANTP | UNKNOWN | 42798 | FACING 802 COMPOSTELA | UNKNOWN | [25 empty] | ELTEK | 53.67 | 0 | 67 | 67 | 4 | 2 | ACME/NARADA | 155 | ACME/NARADA | 155 | NONE | NONE | NONE | NONE | No |  | 48 | 47.7 | NONE | NONE | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | LTE 4G TDD | 63 | BTS3900 LOWER | 63 | BTS3900 UPPER | 63 | BTS3900 3G | 63 | SPARE | 40 | RTN980 MAIN FACING 805 DANAO | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 16 | RTN950 MAIN FACING TAYTAY | 16 | FMS | 16 | CMM | 16 | ECI RAP 4B SOURCE A | 16 | AVIAT A | 16 | SPARE | 16 | BRO ROUTER | EMERSON | 54.5 | 0 | 18 | 18 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | NONE | NONE | No |  | 50.1 | 50.2 | NONE | NONE | Off | 6 | RTN950 REDUNDANT FACING GUINSAY | 16 | ECI RAP 4B SOURCE B | 16 | ERICSSON MINILINK | 16 | BOSER ROUTER | 16 | RTN980 REDUNDANT FACING 805 DANAO | 16 | RTN950 DANAO GUINSAY MAIN | 16 | ALLIED SWITCH TURBO | 50 | FMS | 50 | RTN950 RED FACING V3487 TAYTAY | 50 | SPARE | 50 | SPARE | 6 | SPARE | [20 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 125 | 125 | 70 | RECTIFIER EMERSON | 30 | ACU1 | 20 | CABIN C.O | 30 | ACU2 | 15 | CABIN LIGHT | 15 | TOWER LIGHT | 15 | PER. LIGHT | 70 | ELTEK1 | 15 | SPARE | 20 | ELTEK2 | [20 empty] | Done | OK | ELTEK SN: 130224100498 EMERSON: 21010705842081EA0053 | PERCIVAL QUIJANO | 42788 | [40 empty] | SUPPORT | ELTEK BATTERY |  | ACME G |  | 155 |  | ACCESS | CABLE CLAMPS | [5 empty] | SUPPORT | CARRIER ACU2 |  |  |  |  | DEFECTIVE
V3552SunLLCGunob2.pdf | V3552 | Sun Lapu-lapu City Gun-ob 2 | 2017-02-10 | Astrobal A. Trozo | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For labeling c/o Refarm(defeciency) | Rectification | excess mats for installation and for pull-out | OK |  | Off |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | emerson for replacement of battery(2 banks narada 100AH) | Off |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | Rectification | port hole for resealant | Rectification | forr major grasscut and excess mats for arda/pull-out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3553SUN_ALANG-ALANG.pdf | V3553 | SUN - Lapu-Lapu City-Alang-alang | 2017-03-14 | Astrobal A. Trozo/Ritchie B. Canales | OK |  | N/A | no combiners | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A | no access point | N/A | IBS site, no panel antenna | N/A |  | N/A |  | Off |  | N/A | mains at Z85 Gaisano Mactan Picosite | OK |  | OK |  | OK |  | N/A | no surge suppressors | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | for rectifier and battery replacement | OK |  | N/A |  | OK |  | N/A | building site | OK |  | N/A |  | Rectification | roofing for rehab | Rectification | excess materials for pull out | OK |  | PERCIVAL B. QUIJANO | B | 42808 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3599 Sun Punta Engano 2 Checklist.pdf | V3599 | Sun Lapu-lapu City Punta Engano 2 | 2017-03-07 | Eddie D. Clave Jr | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Rectification | No line of sight due to new building obstruction | N/A |  | OK |  | OK |  | OK |  | Rectification | for relabelling | Rectification | For regrooming of external alarm cable | OK |  | Rectification | For regrooming c/o Huawei | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Rectification | for cleaning of van floor c/o CSMP | OK |  | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3604 Danao Sabang.pdf | V3604 | Danao Sabang | 2017-02-23 | G. VALE | OK | ALL 1.1 TO 1.4. | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | DONE FOR 3G | OK | -36dBm for Aviat and RTN950. | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A | no cmm/router. | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK | NO ATS. | OK |  | OK |  | OK |  | OK |  | OK |  | PERCIVAL QUIJANO | A | 2017-02-23 | BRGY SABANG, DANAO CITY NEAR MITSUMI | COMMERCIAL | LOT | PERMANENT | LOT | 4 LEGGED SST 40M | VAN | 24 H | CARETAKER | Yes | 2017 | UNKNOWN | UNKNOWN | 124.0275 | 10.4894 | UNKNOWN | 1, 4 | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | For Rectification | For Rehab | OK | OK | 4, 0 | OK | Ok | 0, 1 | OK | OK | OK |  | WACU | WACU | Off | FP-51PMXRACCARP19KEDP3C | WCONX019ED1 | NONE | 51PMXRACCAR19KEDR07PC-0433404 | 51QSXRACCON19KEDB15PC-0154357 | NONE | Working | Working | None | 6.9 | 7.4 | NONE | ERICSSON TELECOOL | NONE | 1, 0 | Working | None | POWERCITY | None | Working | 25 | Working | CF100 | 43.4 | Working | 102144 | None | None | 250 L | UNREADABLE | Working | 1 | Working | POWERCITY SN: G14070861 | BTS3900 | Retrieved | BTS3900 | Retrieved | BTS3900 | Retrieved | NONE | Off | NONE | Off | NONE |  | Retrieved | None | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | AVIAT | ECLIPSE | Yes | 13171 | 12905 | -30/-36 dBm | OK | OK | Yes | FACING 805 | HUAWEI | RTN950 | No | to follow | to follow | to follow | OK | OK | Yes | FACING 805 | HUAWEI | RTN950 | No | to follow | to follow | to follow | OK | OK | Yes | FACING V3480 | ERICSSON | MLE | No |  |  | -37dBm | Off | Off | Off | FOR DECOM FACING V3480 | NONE |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE |  |  |  | NONE |  |  |  | NONE |  |  |  | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off | NONE |  | Off | Off | Off |  |  | 2017-03-04 | V3604 SABANG MITSUMI 2G 1800 2XE1 | 6 | 823 MITSUMI 2G 900 1XE1 | 5 | V3480 SUN COMSPOETELA | [6 empty] | ERICSSON MLE | 1 | V3480 SUN COMPOSTELA 2G 1XE1 | [12 empty] | NONE | [10 empty] | AVIAT DAC ES FACING 805 DANAO | 1 | VACANT | 2 | V3530 DANAO SABANG 3G (TO umpt) | 3 | VACANT | 4 | VACANT | [14 empty] | NONE | [19 empty] | NONE | [29 empty] | ELTEK | 54.6 | 0 | 30 | 30 | 4 | 2 | SACRED SUN | 180 | SACRED SUN | 180 | NONE | NONE | NONE | NONE | Off |  | 50.9 | 50.9 | NONE | NONE | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | 2G 900 | 63 | BTS3900 3G | 40 | SPARE | 40 | SPARE | 40 | SPARE | 20 | HSTX B | 20 | HSTX A | 20 | RTN950 MAIN FACING COMPOSTELA | 20 | SPARE | 10 | RTN950 RED FACING DANAO | 10 | SPARE | [15 empty] | Off | [5 empty] | Off | 16 | ERICSSON MLE | 16 | SPARE | 16 | RTN950 RED FACING COMPOSTELA | 16 | SPARE | 10 | RTN950 RED FACING DANAO | 10 | EXHAUST FAN | 10 | EXHAUST FAN | 40 | HUAWEI OUTDOOR BTS | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 25 | SPARE | 25 | SPARE | 25 | SPARE | 25 | SPARE | [6 empty] | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 |  | 20 | LIGHTING/EMERGENCY LIGHT | 60 | RECTIFIER EMERSON1 | 20 | C.O | 60 | RECTIFIER EMERSON2 | 30 | ACU1 | 30 | ACU2 | 20 | OB LIGHT | 20 | PER. LIGHT | 30 | SPARE | 20 | SPARE | 70 | ELTEK1 | 70 | ELTEK2 | [16 empty] | Done | OK | ELTEK1 SN: 120124100261 EMERSON SN: A084054063 | PERCIVAL QUIJANO | 2017-02-23 | [40 empty] | SUPPORT | NO ATS |  |  |  |  | NO ATS | SUPPORT | NO DAY TANK |  |  |  |  | NO DAYTANK
V3675-SUN SOGOD-01272017.pdf | V3675 | SUN SOGOD POBLACION | 2017-01-27 | LEMUEL BALBUENA | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK | NO DISPLAY | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Poblacion, Sogod, Cebu | COMMERCIAL | LOT | PERMANENT | LOT | GUYED 150FT | VAN | 24HRS | CARETAKER | Yes |  | JACINTO MAKILING |  |  |  |  | DEFECTIVE | OK | OK | OK | OK |  | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 2017-02-02 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA | CONDURA |  | N14pc-'0568093 | N14PC-'0568118 |  | Working | Working | Off | 8 | 8 |  |  |  | N/A | Off | Off | N/A | None | None | N/A | None | CF100 | N/A | None |  | None | None | NA |  | Off | NA | Off |  | HUAWEI | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | ERRICSON | MINI-LINK | No |  |  |  | OK | OK | No | CATMON |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | SOGOD | 1 | 2G | [109 empty] | EMERSON | 52.4 | 0 | 22 |  | 4 | 4 | ACME | 100 | ACME | 100 | ACME | 100 | ACME | 100 | Off |  | 53 | 52.8 | 52.7 | 52.5 | OK | [10 empty] | 10 | DC FAN | [10 empty] | 40 | ERRICSON | 40 | BTS3012 | 40 | BTS3012 | [31 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 8.7 | 20 | LIGHTNINGS | 50 | RECTIFIER | 20 | C.OUTLET | 50 | RECTIFIER | 30 | ACU 2 | 30 | ACU1 | 20 | P.LIGHT | 20 | OB LIGHT | 20 | ALARM SYSTEM | 30 | SPARE | [20 empty] | Done | OK |  |  |  | AIRCON | 1 | CARRIER/B07PC-0023459 | WFM
V3687_SUN_Umapad_PMR.pdf | V3687 | SUN Mandaue City - Umapad | 2017-04-02 | Jerome T. Butong | OK | On going refarming activity | N/A |  | Rectification | for busbar installation (indoor and outdoor) | N/A |  | N/A |  | OK |  | Rectification | no busbar | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK | building site | N/A | building site | OK |  | Rectification | No more bus bar | OK |  | OK | excess materials from re-farming still on site | OK |  |  | Off |  | SA Macceb Bldg., Plaridel St., Brgy. Alang2x, Mandaue City | Commerial | Ground floor |  | Building | 40 ft. |  | 9am-6pm | Roving guard | Off |  | Sherwin Ang | 9228638395 |  |  |  |  | N/A | N/A | OK | For CSMP Endo | For VAN cleaning by CSMP | Defective | OK | OK | For Rehab | OK | For Rehab | For Rectification | OK | OK | OK |  | OK | For Rehab |  | OK | For Rectification | For CSMP Endo |  | WACU | WACU | Off | [6 empty] | Working | Working | None | 7.1 A | 0 |  |  |  |  | Working | None |  | None | None |  | None | CF200 |  | Working |  | None | None |  |  | Off |  | None | No genset | Huawei | Retrieved | Huawei | Retrieved | Huawei | Retrieved |  | Off |  | Off |  |  | Off | Off | Huawei | Retrieved |  | Off |  | Off | 2G = 900&1800; 3G = 2100 & 900; FDLTE = 850; | OK | OK | Hauwei | RTN950 | No |  |  |  | OK | Off | Yes | V5139 SUN Paknaan | Huawei | RTN950 | No |  |  |  | OK | Off | Yes | V3699 SUN Opao |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [40 empty] | Facing V5139 SUN Paknaan | S1 P1 | V3687 SUN Umapad 3G | S1 P2 | V3699 SUN Opao 2G/3G/LTE | S1 P3 | V3687 SUN Umapad 2G | S1 P4 | V3687 SUN Umapad LTE | [12 empty] | Facing V3699 SUN Opao | S1 P1 |  | S1 P2 |  | S1 P3 | V3699 SUN Opao 2G/3G/LTE | S1 P4 | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Done | OK
V3695SunPajo2.pdf | V3695 | SUN - Lapu-Lapu City-Pajo 2 | 2017-02-27 | Astrobal A. Trozo | OK |  | N/A | no combiners | N/A | STOLEN BUSBAR | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A | no access point | OK |  | N/A |  | N/A |  | Rectification | for huawei rectification | OK |  | N/A | stolen outdoor busbar | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | for replacement of battery | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Rectification | stolen outdoor busbar | OK | excess refarming materials for pull out c/o huawei; acu's for pull out | OK |  | PERCIVAL B. QUIJANO | B | 2017-02-27 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3703 SUN Mandaue City Cabancalan.pdf | V3703 | Sun Mandaue City Cabancalan | 2017-01-28 | Eric Brian Aligway | OK |  | N/A |  | Rectification | All tower busbar and grounding ar stolen | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | No external alarms | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK | All tower busbar and grounding are stolen | OK |  | OK |  | OK |  |  | B |  | Brgy. Cabancalan |  |  | Commercial Permanent |  | Guyed tower/120 ft. | Collapsible Van | 24/7 |  | Yes |  | Benjie Antolijao |  | 123.9276 | 10.3557 |  | Busted | OK | OK | OK | For CSMP Endo | For CSMP PMR | Working | OK | OK | OK | OK | For Rehab | OK | For Rehab | Expired | OK | WO | OK | Ok | Def. | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONX019ED1 | PF-51PMXRACCARP19KEDP3C |  | 51QSXRACCON19KED K15PC-0540074 | 51PMXRACCAR19KEDT07PC-0500700 |  | Working | Defective | Off | [5 empty] | N/A | None | Off | N/A | None | Working | N/A | None | CF200 | N/A | Working | 40041981 | None | Off | NONE |  | Off | NONE | None |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off | Huawei | RTN950 | Yes | 14963/14991/14935 | 14543/14571/14515 | -0.028188 | OK | OK | No | V3716 SUN Mandaue City Casuntingan2 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [43 empty] | 2 | 2G(G1800) | 3 | 3G(U2100,U900) | 4 | LTE(L850) | [64 empty] | Emerson | 54.5V |  |  | 47A | 5 | 3 | SacredSun | 150 | SacredSun | 150 | SacredSun | 150 |  |  | No | 3 | 54.3 | 54.1 | 54..3 |  | OK | 63 | RTN950 A |  |  | 63 | RTN950A | [6 empty] | 80 | DCDU A | 80 | DCDU B | [43 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 125 |  | 70 | Rectifier | 30 | ACU1 | 20 | C.O | 30 | ACU2 | 15 | Lighting | 15 | OB light | 15 | Perimeter | 20 | Spare | 15 | Spare | 20 | Spare | [20 empty] | Done | OK |  |  | 42763
V3722_Babag_2.pdf | V3722 | Sun Lapu-lapu City Babag 2 | 2017-02-22 | Astrobal Trozo | OK |  | OK |  | Rectification | antenna grounding not connected at clamp. No busbar on top | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For re-labeling | Rectification | excess materials for ARDA | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | For replacement of battery on Emerson rectifier | OK |  | OK |  | OK |  | N/A |  | Off |  | OK |  | Rectification | excess material for pull-out/ARDA; for cleaning | Rectification | major grasscutiing and pull-out garbage | OK |  |  | B | 2017-02-22 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3723 Sun LLC-Mactan Doctor's Hospital.pdf | V3723 | SUN-Lapu Lapu-Mactan Doctors Hospital | 2017-02-20 | Astrobal A. Trozo | OK |  | OK |  | N/A | no busbar, stolen | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | waiting for IT for the huawei software installation | N/A | waiting for IT for the huawei software installation | Rectification | for huawei rectification | OK |  | N/A | no busbar, stolen | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A | building site | OK |  | OK |  | Rectification | no busbar | Rectification | excess materials for pull out; 1 acu for arda(no serial number) | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V3726 Sun LLC Maribago 2 Checklist.pdf | V3726 | Sun Lapu-lapu City Maribago 2 | 2017-02-21 | EDDIE D. CLAVE JR. | OK |  | OK |  | Rectification | stolen grounding busbar | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Rectification | For re-labelling | Rectification | no mains for isolation and cabling | Rectification | stolen grounding busbar | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | unclean surrounding and excess mats on site | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V5128 SM Consolacion2.pdf | V5128 | SM Consolacion2 | 2017-02-16 | A. Ambil | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | Rectification | NO BACK-UP. BLOATED BATTERY | OK | NO BACK-UP. BLOATED BATTERY | N/A |  | OK |  | N/A |  | OK |  | N/A | INDOOR SITE | OK |  | N/A |  | OK |  | PERCIVAL QUIJANO | A | 2017-02-16 | SM Consolacion cinema, SM City Consoalcion, Consolacion, Cebu | Commercial | Cinema | SUBMETER | Building | N/a | ROOM | Mall hours | Admin | Yes |  | SM Consolacion | N/A |  |  | SM Consolacion | N/A | N/A | N/A | OK | For CSMP Endo | INDOOR SITE | Working | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4, 0 | OK | Ok | 0, 1 | OK | OK | OK |  | Split Type | Split Type | Off | 42LUC022308/CARRIER | 42LUC022308/CARRIER |  | UNREADABLE | UNREADABLE |  | Defective | Defective | Off | 0 | 0 |  |  |  | 0, 0 | None | None | N/A | None | Off | N/A | None | Off | N/A | None | N/A | None | None | N/A | N/A | Off | N/A | None |  | BTS3900 | Retrieved |  | Off | BTS3900 | Retrieved | NONE | Off | NONE | Off | NONE |  | Off | Off | NONE | Off | NONE | Off | NONE | Off |  | OK | OK | NONE |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  | NONE |  | Off |  |  |  | Off |  | Off |  | NONE | [11 empty] | ECI | XDM-100 | Yes | Trad | Yes | ZTE | ZXMP M721 | Yes | Trad | Yes |  |  | Off | Off | Off |  | XDM-100 | i1-1 | v5128 2g 1st e1 | [36 empty] | zte fs | slot10- c2 opt | V5128 3G VIA ZTE FS | [39 empty] | OPS CORE 1/2 | FACING V0907 SM CONSOLACION1 | [29 empty] | ELTEK | 54.4 V | 0 | 17 | 17 | 4 | 3 | LYNX | 170 | LYNX | 170 | LYNX | 170 | NONE | NONE | Off | [5 empty] | Off | 100 | SPARE | 100 | SPARE | 100 | SPARE | 100 | SPARE | 80 | SPARE | 80 | SPARE | 80 | SPARE | 80 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | V5128 2G | 40 | SPARE | 40 | WCDMA | 40 | XDM-100 A | 40 | XDM-100 B | 20 | ZTE FS MAIN | 20 | ZTE FS REDUNDANT | 20 | SPARE | 10 | SPARE | 10 | SPARE | [17 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK1 | 70 | ELTEK2 | 30 | ACU1 | 30 | ACU2 | 20 | LIGHTINGS | 20 | EMERGENCY LIGHT | 20 | SPARE | 20 | OULTLET | 20 | SPARE | 20 | SPARE | [20 empty] | Done | OK | ELTEK SN: 120124100394 | [42 empty] | SUPPORT | ACU DEFECTIVE |  | CARRIER |  |  | UNKNOWN | SUPPORT | BATTERY 3 BANKS DEF |  | LYNX |  | 170AH | N/A
V5155 SUN CEBU CITY UP COLLEGE-03252017.pdf | V5155 | SUN CEBU CITY UP COLLEGE | 2017-03-25 | LEMUEL BALBUENA | OK |  | N/A |  | Rectification | STOLEN OUTSIDE GROUNDING | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  |  | COMMERCIAL | LOT | PERMANENT | LOT | GUYED 80FT | VAN | 24HRS | ROVING GUARD | Off | [6 empty] | NOT WORKING | OK | for CSMP Endo | OK | For CSMP Endo |  | Off | Off | Off | Off | Off | Off | Off | OK | OK | OK | 36617 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA/WCONX019ED1 | CARRIER/FP-51PMXRACCAR19KEDP3C |  | 51QSXRACCON19KEDT15PC-0741484 | 51PMXRACCAR19KEDT07PC-0479320 |  | Working | Defective | Off | 9 |  |  | URA |  |  | Working | Off |  | None | None |  | None | CF200 |  | None |  | Off | None |  |  | Off |  | Off | INHOUSEA1 | HUAWEI | Retrieved |  | Off | HUAWEI U2100/900 | Retrieved |  | Off |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | OK | OK | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | LAHUG | HUAWEI | RTN620 | No |  |  |  | OK | OK | Yes | FACING CEB012 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 2G | 2 | LTE | 3 | 3G | 4 | P2 RTN 620 | [64 empty] | ELTEK | 54 | 3 |  |  | 57 | 4 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | SACREDSUN | 180 | No |  | 52.2 | 51.9 | 51.5 | 51.2 | OK |  |  |  |  | 100 | DCDU L850/G900 | 100 | DCDU G1800/U2100 | [10 empty] | 40 | SMART 3G | [22 empty] | 16 | RTN950 MAIN | EMERSON | 53.5 |  |  | 4 | 4 | 3 | SACREDSUN | 150 | SACREDSUN | 150 | SACREDSUN | 150 |  |  | No |  | 52.7 | 52.6 | 52.6 |  | OK |  |  |  |  | 16 | RTN950 REDUNDANT |  |  | 40 | 3G | [49 empty] | Off | [5 empty] | Off | [44 empty] | 175 | 24.5 | 20 | LIGHTING | 70 | RECTIFIER | 30 | C.O | 30 | ACU 1 | 30 | ACU 2 | 20 | O.B LIGHT | 20 | PERIMETER LIGHTS | 20 | ALARM SYSTEM | 70 | ELTEK 1 | 60 | ELTEK 2 | [20 empty] | Done | OK
V5267 CEBU GRAND CENIA-03132017.pdf | V5267 | Cebu Grand Cenia | 2017-03-13 | Lemuel Balbuena | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | OK |  | N/A | building site | OK |  | OK |  | OK |  |  | Off |  | Blk18 Lot1-7, Archbishop Reyes cor Apitong, Brgy. Hippodromo, Cebu City | Commercial | 3rd Floor Building | Tap to Lessor | Building | pico site | room | 8am-5-m | Admin/Bldg Security | Yes |  |  |  | 123.903 | 10.32 |  | 36557 | N/A | N/A | N/A | OK | building site | Off | Off | Off | Off | Off | Off | Off | OK | OK | OK | working | OK | Ok | working | OK | OK | Off |  | PACU | PACU | Off | Koppel | Carrier |  |  |  |  | Defective | Defective | Off | [6 empty] | None | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  | Huawei | Retrieved |  | Off | Huawei | Retrieved |  | Off |  | Off |  |  | Off | Off | Huawei | Retrieved |  | Off |  | Off |  | Off | Off | Harris | Stratex | Yes |  |  |  | OK | OK | Yes | z90 Mabolo |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off |  | z90 Mabolo DAC-ES | 1 | LTE | 2 | 3G | [8 empty] | Z90 | 1 | 2G | [96 empty] | Eltek Valere | 53.17 |  |  | 25 | 4 | 3 | SACRED SUN | 150 | SACRED SUN | 150 | SACRED SUN18 | 150 |  |  | No |  | 52.2 | 52 | 51.9 |  | Off | [8 empty] | 80 | -48 POWER | [14 empty] | 40 | 3G/LTE | [33 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 4.1 | 60 | ELTEK 1 | 60 | SPARE | 60 | ELTEK 2 | 60 | SPARE | 30 | SPARE | 30 | SPARE | 30 | SPARE | 30 | ACU 2 | 30 | EMERGENCY LIGHT | 20 | SPARE | 30 | PLDT MAIN RECTIFIER | 20 | C.OUTLET | [16 empty] | Done | OK | HI-TEMP
V5273 IT Park.pdf | V5273 | IT Park | 2017-03-13 | Eric Brian Aligway | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | Off |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK | Need additional battery banks and RM | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | Percival Quijano | B | 42807 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V5308 JCenter_040417.pdf | V5308 | J Center Mall | 2017-04-04 | Jerome T. Butong / Rodyard Efe | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | N/A | Pico site | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | N/A | no router | OK |  | OK |  | N/A |  | N/A | no ODF | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A | no genset | OK | Indoor. Tap to Mall | N/A | IBS | OK |  | OK | Unused Emerson 2G equipment and microwave antenna still inside the van | OK |  | Percival B. Quijano | B |  | Basement 1,J Center Mall, A.S. Fortuna St., Mandaue City | Commercial | Basement | Permanent | Building | no tower | Van | Mall Hours | Roving Guard | Yes | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | TO FOLLOW | N/A | N/A | N/A | OK | For CSMP Endo | For CSMP cleaning inside the van | Working | OK | OK | OK | OK | OK | For Rectification | OK | OK | OK | 2 of 2 working | OK | Ok | not working | OK | OK | For CSMP Endo |  | WACU | WACU | Off | WCONA019ED | WCONA019ED |  | A12PC-0012810 | A12PC-0012805 |  | Defective | Working | None | 0 | 7.09 A |  |  |  |  | None | None |  | None | None |  | None | CF200 |  | None |  | None | None |  | TO FOLLOW | For CSMP Endo |  | None | No genset | BTS3900 | Retrieved |  | Off | BTS3900 | Retrieved |  | Off |  | Off |  |  | Retrieved | Off | BTS3900 | Retrieved |  | Off |  | Off | 2G: 1800; 3G: U2100; FDLTE: L850 | OK | OK | AVIAT | Stratex | No | 12947 / 12905 | 13213 / 13171 | no reading / -49bdm | OK | Off | Yes | 846 Bakilid |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | No |  |  |  | Off | Off | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | No |  |  |  | OK | OK | Yes | NA |  |  | Off |  |  |  | Off |  | Off | NA | [14 empty] | Yes | Off | Yes |  |  | Yes | Off | Yes |  |  | Yes | Off | No | [40 empty] | Aviat facing Bakilid | S6 - P3 | V5308 J Center 2G | S6 - P2 | V5308 J Center 3G | S3 - P2 | V5308 J Center FD-LTE | [66 empty] | ELTEK | 54.43 V | 0 | 46 A | 46 A | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | No |  | 53.81 | 53.81 | 53.81 | 53.81 | OK | 100 | DCDU for Refarming | 100 |  | 100 |  | 100 |  | 80 | BTS3900 for 2G | 80 | BTS3900 for 3G/LTE | 80 |  | 80 |  | 63 |  | 63 |  | 63 |  | 63 |  | 40 | Harris A | 40 | Harris B | 40 | LTE DCDU (for RRU) | 40 |  | 20 |  | 20 |  | 20 |  | 20 |  | 10 |  | 10 | [16 empty] | No | [5 empty] | OK | [59 empty] | Off | [5 empty] | Off | [44 empty] | 100 | 100 | 70 | ELTEK A | 70 | ELTEK B | 30 | ACU 2 | 30 | ACU 1 | 30 |  | 30 |  | 30 | Emergency Light | 30 | C. O. | 20 |  | 20 | Lighting | [20 empty] | Done | OK |  | PERCIVAL B. QUIJANO | 42800 | Emerson BTS cabinet | 1 |  |  | Microwave Antenna | 1
V5312-CEBU KALUNASAN-02282017.pdf | V5312 | CEBU KALUNASAN | 2017-02-28 | LEMUEL BALBUENA | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | DEFECTIVE GENSET/NO ATS | OK |  | OK |  | OK |  | OK |  | OK |  |  | Off |  | Sitio Tagaytay Kalunasan Guadalupe Cebu City | COMMERCIAL | LOT | PERMANENT | LOT | SST 150FT | ROOM | 24HRS | CARETAKER | Off | [6 empty] | Defective | OK | OK | OK | OK |  | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 36678 | OK | Ok | WORKING | OK | OK | OK |  | WACU | WACU | Off | CONDURA/FP-51QSXRACCONA19KEDP1C | CONDURA/WCONA019ED |  | 51QSXRACCON19KEDA11PC-0010180 | 51QSXRACCON19KEDA11PC-0075468 |  | Working | Working | Off | 8 | 7.9 |  | OMNI |  | DEFECTIVE | Working | Off | DENYO | None | None | 25 | None | CF200 |  | None |  | None | Off |  |  | For CSMP Endo |  | None |  | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved | HUAWEI | Retrieved |  | Off |  |  | Off | Off | HUAWEI | Retrieved |  | Off |  | Off |  | Off | Off | HUAWEI | RTN950 | Yes |  |  |  | OK | OK | Yes | MSC3 | HARRIS | STRATEX | Yes |  |  |  | OK | OK | Yes | MSC3 |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [41 empty] | 1 | 2G | 3 | 3G | 4 | LTE | [66 empty] | ELTEK | 54.3 | 0 |  | 27 | 4 | 4 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | SACRED SUN | 180 | Off |  | 53.3 | 53.2 | 53.1. | 53 | OK | 100 | DCDU G900 |  |  |  |  | 100 | BTS 3900 LOWER | [18 empty] | 40 | 3G/LTE DCDU | 40 | AVIAT MAIN | 20 | HUAWEI RTN950 MAIN | [12 empty] | ELTEK | 53.93 | 0 |  | 38 | 4 | 2 | ACME |  | ACME | [5 empty] | Off |  | 50 | 49.9 |  |  | Off | [6 empty] | 100 | DCDU L700/U1800 | 100 | DCDU G1800/L850 |  |  |  |  | 80 | BTS3900 UPPER | [14 empty] | 40 | AVIAT PROTECTION | 20 | HUAWEI RTN950 REDUNDANT | [25 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 34.7 | 70 | ELTEK A1 | 70 | ELTEK B1 | 70 | ELTEK A2 | 15 | TOWER LIGHT | 40 | SPARE | 20 | CABIN LIGHT | 40 | SPARE | 20 | OUTLET | 40 | ACU1 | 30 | PERIMETER LIGHT | 40 | ACU2 | 30 | ELTEK B2 | [16 empty] | Done | OK | [133 empty] | defective
V6602SMAguaVerde.pdf | V6602 | SM Agua Verde | 2017-03-20 | Astrobal A. Trozo | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A | Inbuilding site, no genset and ATS | OK |  | OK |  | OK |  | N/A | excess materials for pull out | OK |  | PERCIVAL B. QUIJANO | B | 42814 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
V6604-Western Lex-03182017.pdf | V6604 | Western Lex | 2017-03-18 | Lemuel Balbuena and Alan Mark Rodrigo | OK |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | Rectification | System Clock Failure | OK |  | OK |  | N/A |  | OK |  | N/A |  | N/A |  | N/A | Pole | OK |  | OK | Located at 3rd Floor of the Hotel | OK |  |  | A | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
W74 CompostelaTP.pdf | W74 | CompostelaTP | 2017-02-06 | G.Vale/A. Ambil | OK | All VSWR 1.1. | N/A | NOT APPLICABLE. | OK | ALL ARE OK. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NO BRO. NOT APPLICABLE. | OK |  | OK |  | Rectification | AVIAT LOW RSL ON GOING RECTIFICATION DURING PMR. | N/A | NOT APPLICABLE. | OK |  | OK | DONE. | Off | RTN950: -38dBm. Aviat: -46dBm- on going antenna panning during PMR. | OK | ok. | OK | Done. | OK |  | OK |  | OK |  | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK | ok. | OK | done. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | N/A | NOT APPLICABLE. | OK | ok for Wimax. | OK | 53.92V, no defective RM. All breakers with label. | OK | 4 hours back-up. | N/A | NOT APPLICABLE. | OK |  | Rectification | Defective ATS fuse, waiting for FSR. | OK |  | OK | On-going rectification of low RSL. | OK |  | Rectification | Need grasscutting. | OK |  | Percival Quijano | A | 42772 | Brgy. Cogon, Compostela, Cebu | Residential | Lot | Permanent | Lot | Guyed 32m | Van | 24 hours | Caretaker | Yes |  | Alex Atillo | NA | 10.4572 | 124.006 | Brgy. Cogon, Compostela, Cebu | 1, 3 | OK | OK | for Replacement | For CSMP Endo | Need grasscutting, padlock at gate for replacement | Defective | OK | OK | OK | OK | OK | OK | OK | OK | OK | 4, 0 | OK | Ok | NONE | OK | OK | Off |  | WACU | Off | Off | WCONX019ED1 | NA | NA | 51QSXRACCON19KED C15PC-0263836 | NA | NA | Working | None | None | 8A | NONE | NA | ASAHI | ASAHI | 1, 0 | Working | Working | KIPOR SN: 0728060043 | Defective | None | 30 | None | CF200 | 45 | None | 38278 | Working | None | 50L | 10064511 | Working | NONE | Working | ATS Kutai SN: 10600, defective fuse | BTS3900L | Retrieved | BTS3900L | Retrieved | BTS3900 | Retrieved | none | Off | 3 | retrieved | none | none | Off | None | none | Off | none | Off | none | Off |  | OK | OK | Huawei | RTN950 | Yes | 13045 13213 13101 | 12779 12947 12835 | -38dBm/-38dBm | OK | OK | Yes | 802 Compostela | Aviat | HSTX | Yes | 12905 | 13171 | -39dBm | OK | OK | Yes | 802 Compostela | NONE |  | Off |  |  |  | Off | Off | Off | NA | NONE |  | Off |  |  |  | Off | Off | Off | NA | NONE |  | Off |  |  |  | Off | Off | Off | NA | NONE |  | Off |  |  |  | Off |  | Off | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  | Off | Off | Off | NA |  | Off | Off | Off | NA |  | Off | Off | Off |  | Aviat facing 802 Compostela | 5 | W74 Compostela Wimax 1st e1 | 6 | W74 Compostela Wimax 2nd e1 | 7 | W74 Compostela Wimax 3rd e1 | 8 | W74 Compostela Wimax 4th e1 |  |  |  |  | NONE | [12 empty] | NONE | [12 empty] | RTN950 facing 802 Compostela | 1 | W74 Compostela 2G (to GTMU) | 2 | W74 Compostela 3G (to WMPT) | [16 empty] | none |  | none | [19 empty] | none | [29 empty] | ELTEK | 53.92 | 1 | 56 | 56 | 4 | 4 | Sacred SUN | 180 | Sacred SUN | 180 | Sacred SUN | 180 | Sacred SUN | 180 | No |  | 53.8 | 53.7 | 53.9 | 53.7 | OK | 100 | BTS3900 UPPER | 100 | BTS3900 LOWER | 100 | BTS3900 | 100 | SPARE | 63 | DCDU 12B/1800 | 63 | SPARE | 63 | SPARE | 63 | SPARE | 63 | SPARE | 40 | TELLABS | 40 | WIMAX ZTE | 40 | SPARE | 40 | SPARE | 40 | SPARE | 40 | HARRIS A | 20 | SPARE | 20 | HARRIS B | 20 | SPARE | 16 | SPARE | 16 | SPARE | 16 | RTN950 REDUNDANT | 16 | RTN950 MAIN | NONE | [14 empty] | Off | [5 empty] | Off | [44 empty] | none | [14 empty] | Off | [5 empty] | Off | [44 empty] | 150 | 150 | 70 | spare | 70 | ELTEK1 | 30 | ACU1 | 30 | ACU2 | 30 | LIGHT | 30 | OUTLET | 20 | PERIMETER LIGHT | 20 | EX FAN | 20 | TOWER LIGHT | 20 | ELTEK2 | [20 empty] | Done | OK |  | Percival Quijano | 42772 | NONE | [39 empty] | SUPPORT | ATS | 1 | KUTAI | 225 A | NA | SN: 10600 | [84 empty] | Defective battery charger
W93SubaMasulog.pdf | W93 | Suba Masulog | 2017-01-18 | Astrobal A. Trozo | OK |  | N/A |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A | no Radio | OK |  | OK |  | N/A | waiting for IT for the installation of Huawei Software | N/A | waiting for IT for the installation of Huawei Software | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | Rectification | major grass cutting and excess materials for pull out | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
Z23 Olango Checklist.pdf | Z23 | Olango | 2017-02-20 | Eddie D. Clave Jr. | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | OK |  | N/A |  | OK |  | OK |  | OK |  | Off |  | OK |  | Rectification | stolen grounding busbar | OK |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | Rectification | for replacement of 2 defective RM | OK |  | OK |  | OK |  | Rectification | Defective genset/ATS. For CSMP checking | OK |  | OK |  | Rectification | excess mats for pull-out | Rectification | excess mats for pull-out; need grass cutting | OK |  |  | Off | [10 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off
Z85GAISANOMACTANPICOSITE.pdf | Z85 | Gaisano Mactan Picosite | 2017-03-14 | Astrobal A. Trozo/Ritchie B. Canales | OK |  | N/A | no combiners | OK |  | N/A |  | OK |  | OK |  | OK |  | OK |  | N/A |  | N/A | no access point | N/A | IBS site, no panel antenna | N/A |  | N/A |  | Off |  | OK |  | OK |  | OK |  | OK |  | N/A | no surge suppressors | N/A |  | OK |  | N/A |  | N/A |  | OK |  | N/A |  | N/A |  | OK |  | OK |  | OK |  | N/A |  | OK |  | N/A | building site | OK |  | N/A |  | Rectification | roofing for rehab | Rectification | MCB for rehab | OK |  | PERCIVAL B. QUIJANO | B | 2017-03-14 | [9 empty] | Off | [7 empty] | Off | Off | Off | Off |  | Off | Off | Off | Off | Off | Off | Off | Off | Off | Off |  | Off | Off |  | Off | Off | Off |  | Off | Off | Off | [6 empty] | Off | Off | Off | [6 empty] | Off | Off |  | Off | Off |  | Off | Off |  | Off |  | Off | Off |  |  | Off |  | Off |  |  | Off |  | Off |  | Off |  | Off |  | Off |  |  | Off | Off |  | Off |  | Off |  | Off |  | Off | Off |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off | Off | Off |  |  |  | Off |  |  |  | Off |  | Off | [15 empty] | Off | Off | Off |  |  | Off | Off | Off |  |  | Off | Off | Off | [128 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [59 empty] | Off | [5 empty] | Off | [86 empty] | Off | Off